## Request a quote
Request a quotation for PROFIBUS PA
Share your protocol/frequency, jacket material (PVC, PUR, LSZH, FEP), and installation motion for PROFIBUS PA.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/profibus-pa-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
PROFIBUS PA Cable – Dimensions & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-pa-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A (PROFIBUS PA / MBP / FISCO). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Conductor size | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| PROFIBUS PA Ex-i Blue PVC 1×2×18 AWG (0.8 mm²) | 1×2×18 AWG (Ex-i Blue PVC) | 0.80 mm² (18 AWG) | 8 | 38 | 76 | 64 | Standard PROFIBUS PA configurations
| PROFIBUS PA Non-Ex Black PVC 1×2×18 AWG (0.8 mm²) | 1×2×18 AWG (Non-Ex Black PVC) | 0.80 mm² (18 AWG) | 8 | 38 | 76 | 64 | Standard PROFIBUS PA configurations
| PROFIBUS PA Ex-i Blue LSZH 1×2×1.0 mm² | 1×2×1.0 mm² (Ex-i Blue LSZH) | 1.0 mm² (17 AWG) | 8.3 | 43 | 84 | 66 | Standard PROFIBUS PA configurations
| PROFIBUS PA Long-Trunk 1×2×1.5 mm² Ex-i Blue | 1×2×1.5 mm² (Long-Trunk Ex-i) | 1.5 mm² (16 AWG) | 9.2 | 54 | 102 | 74 | Standard PROFIBUS PA configurations
| PROFIBUS PA SWA Armoured 1×2×18 AWG (0.8 mm²) | 1×2×18 AWG (SWA Armoured) | 0.80 mm² (18 AWG) | 12.4 | 38 | 245 | 99 | Standard PROFIBUS PA configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per IEC 61158-2 Type A (PROFIBUS PA / MBP / FISCO).

## Impedance, capacitance & attenu
PROFIBUS PA Cable – Impedance, capacitance & attenuation (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-pa-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A (PROFIBUS PA / MBP / FISCO). Values for your order are confirmed in the quotation.
Configuration | Impedance Z0 | Max. DC R @ 20 °C Ω/km | Mutual C pF/m ≈ | VoP % | Attenuation @ 20 °C dB/100m | Dielectric test V
1×2×18 AWG (Ex-i Blue PVC) | 100 Ω | 44 | 48 | 68 | 0.28 dB/100m @ 39 kHz | 1500
1×2×18 AWG (Non-Ex Black PVC) | 100 Ω | 44 | 48 | 68 | 0.28 dB/100m @ 39 kHz | 1500
1×2×1.0 mm² (Ex-i Blue LSZH) | 100 Ω | 36 | 50 | 68 | 0.25 dB/100m @ 39 kHz | 1500
1×2×1.5 mm² (Long-Trunk Ex-i) | 100 Ω | 24.4 | 52 | 68 | 0.21 dB/100m @ 39 kHz | 1500
1×2×18 AWG (SWA Armoured) | 100 Ω | 44 | 48 | 68 | 0.28 dB/100m @ 39 kHz | 1500
Transmission values (characteristic impedance Z0, mutual capacitance, VoP, and attenuation) are measured at +20 °C per IEC 61158-2 Type A (PROFIBUS PA / MBP / FISCO).

## Technical data
PROFIBUS PA Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-pa-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A (PROFIBUS PA / MBP / FISCO). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Impedance Z0 | 100 Ω ± 20 Ω (Measured at 31.25 kHz (MBP))
Key data | Conductor size | 18 AWG (0.8 mm²) (Also available in 1.0 & 1.5 mm²)
Key data | Loop resistance | ≤ 44 Ω / km (22 Ω/km per core (18 AWG))
Key data | Attenuation | ≤ 3.0 dB / km (At 39 kHz (≤ 0.30 dB/100m))
Key data | FISCO inductance | 0.4–1.0 mH/km (L/R & C within IEC 60079-27 FISCO)
Key data | Max. trunk reach | Up to 1,900 m (Non-Ex 1900 m · Ex-ia FISCO 1000 m)
Electrical | Characteristic impedance Z0 | 100 Ω ± 20 Ω at 31.25 kHz
Electrical | Max. DC loop resistance @ 20 °C | ≤ 44 Ω/km (18 AWG / 0.8 mm²) · ≤ 24.4 Ω/km
Electrical | Mutual capacitance @ 1 kHz | ≈ 45–55 pF/m (standard limit ≤ 60 nF/km)
Electrical | Attenuation @ 39 kHz | ≤ 3.0 dB/km (≤ 0.30 dB/100m)
Electrical | FISCO parameters (R', L', C') | R' = 15–150 Ω/km · L' = 0.4–1.0 mH/km · C'
Electrical | Velocity of propagation & test V | ≈ 68 % (0.68 c) · 300 V rating / 1.5 kV AC
Thermal | Operating temp. (fixed) | -40 °C to +80 °C (+105 °C heat-resistant
Thermal | Installation temperature | -20 °C to +60 °C
Mechanical | Nominal outer diameter | 8.0 mm (1×2×18 AWG unarmoured) · 12.4 mm
Mechanical | Min. bending radius | 8 × D unarmoured · 12 × D SWA armoured
Resistance | Hydrocarbon, oil & UV resistance | EN 60811-404 · UL Sunlight Resistant
Resistance | Flame retardancy | IEC 60332-1-2 & IEC 60332-3-24 Cat C
Standards | Primary specification | IEC 61158-2 Type A (MBP-IS / PROFIBUS PA)
Standards | Intrinsic safety validation | IEC 60079-14 & IEC 60079-27 / IEC 60079-11
Identification | Core colours | Red (PA+) · Green (PA-) — or Blue/Brown per
Identification | Outer sheath colour | RAL 5015 Blue (Ex-i) or RAL 9005 Black

## Construction
PROFIBUS PA Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-pa-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A (PROFIBUS PA / MBP / FISCO). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded copper conductor pair | 18 AWG (0.80 mm², 7×0.38 mm or 19×0.23 mm) or 1.0 / 1.5 mm² bare or tinned copper | IEC 61158-2 Type A
2 | Polyethylene / foam-skin PE dielectric | Low-loss PE / O2YS insulation tuned to Z0 = 100 Ω at 31.25 kHz and C < 60 pF/m | IEC 61158-2
3 | Static screen (Al/PET + drain) | Aluminium/polyester tape (100 % coverage) with 0.5 mm² tinned copper drain wire | IEC 61158-2 Type A
4 | EMC tinned copper braid | Tinned copper wire braid, optical coverage ≥ 80 % (≥ 90 % overall shield coverage) | IEC 61158-2
5 | Process outer sheath | Hydrocarbon-resistant PVC, PUR, or LSZH in RAL 5015 Sky Blue (Ex-i) or RAL 9005 Black | EN 60079-14 / IEC 60332-3
| PROFIBUS PA Ex-i Blue (RAL 5015) | FISCO-compliant intrinsically safe (Ex ia / Ex ib) blue cable for ATEX/IECEx Zone 0, 1 & 2.
| PROFIBUS PA Non-Ex Black & SWA Armoured | UV-resistant black PVC/PUR/LSZH or galvanized steel-wire armoured (SWA) process trunk cable.

## Quality and supply
PROFIBUS PA Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/profibus-pa-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A (PROFIBUS PA / MBP / FISCO). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 31.25 kHz impedance Z0 & 39 kHz attenuation — Z0 = 100 ± 20 Ω at 31.25 kHz; attenuation ≤ 3.0 dB/km | 100 % of reels
Routine test | FISCO R', L', C' verification & 1.5 kV AC test — R' ≤ 44 Ω/km, L' = 0.4–1.0 mH/km, C' ≤ 60 nF/km | 100 % of reels
Sample test | Capacitive unbalance to screen — ≤ 2 nF/km per IEC 61158-2 Type A | Per production batch
Type test | Bunched flame test & hydrocarbon resistance — IEC 60332-3-24 Cat C & EN 60811-404 | Type approval
Standard / approval | IEC 61158-2 Type A
Standard / approval | IEC 60079-11 / 60079-27 FISCO
Standard / approval | UL PLTC / ITC / CMG
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX PROFIBUS PA IEC 61158-2 TYPE A
Supply | Delivery form: Non-returnable plywood reels or export drums
Supply | Standard reel lengths: 100 m · 305 m · 500 m · 1000 m
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP