## Request a quote
Request a quotation for PROFINET Type A
Share your protocol/frequency, jacket material (PVC, PUR, LSZH, FEP), and installation motion for PROFINET Type A.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/profinet-type-a-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
PROFINET Type A Cable – Dimensions & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-a-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-5 / PNO Guideline 2.142 (Type A). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Conductor size | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| PROFINET Type A FC PVC 2×2×AWG22/1 | 2×2×AWG22/1 (PVC FC) | AWG 22/1 (0.64 mm) | 6.5 | 32 | 61 | 26 | Standard PROFINET Type A configurations
| PROFINET Type A FC PUR 2×2×AWG22/1 | 2×2×AWG22/1 (PUR FC) | AWG 22/1 (0.64 mm) | 6.5 | 32 | 60 | 26 | Standard PROFINET Type A configurations
| PROFINET Type A FC FRNC/LSZH 2×2×AWG22/1 | 2×2×AWG22/1 (LSZH FC) | AWG 22/1 (0.64 mm) | 6.5 | 32 | 63 | 26 | Standard PROFINET Type A configurations
| PROFINET Type A Underground PE 2×2×AWG22/1 | 2×2×AWG22/1 (PE Burial) | AWG 22/1 (0.64 mm) | 6.5 | 32 | 54 | 26 | Standard PROFINET Type A configurations
| PROFINET Type A SWA Armoured 2×2×AWG22/1 | 2×2×AWG22/1 (SWA Armoured) | AWG 22/1 (0.64 mm) | 10.8 | 32 | 195 | 43 | Standard PROFINET Type A configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per IEC 61156-5 / PNO Guideline 2.142 (Type A).

## Impedance, capacitance & attenu
PROFINET Type A Cable – Impedance, capacitance & attenuation (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-a-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-5 / PNO Guideline 2.142 (Type A). Values for your order are confirmed in the quotation.
Configuration | Impedance Z0 | Max. DC R @ 20 °C Ω/km | Mutual C pF/m ≈ | VoP % | Attenuation @ 20 °C dB/100m | Dielectric test V
2×2×AWG22/1 (PVC FC) | 100 Ω | 115 | 48 | 65 | 2.1 @ 1 · 6.0 @ 10 · 19.5 @ 100 MHz | 2000
2×2×AWG22/1 (PUR FC) | 100 Ω | 115 | 48 | 65 | 2.1 @ 1 · 6.0 @ 10 · 19.5 @ 100 MHz | 2000
2×2×AWG22/1 (LSZH FC) | 100 Ω | 115 | 48 | 65 | 2.1 @ 1 · 6.0 @ 10 · 19.5 @ 100 MHz | 2000
2×2×AWG22/1 (PE Burial) | 100 Ω | 115 | 48 | 65 | 2.1 @ 1 · 6.0 @ 10 · 19.5 @ 100 MHz | 2000
2×2×AWG22/1 (SWA Armoured) | 100 Ω | 115 | 48 | 65 | 2.1 @ 1 · 6.0 @ 10 · 19.5 @ 100 MHz | 2000
Transmission values (characteristic impedance Z0, mutual capacitance, VoP, and attenuation) are measured at +20 °C per IEC 61156-5 / PNO Guideline 2.142 (Type A).

## Technical data
PROFINET Type A Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-a-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-5 / PNO Guideline 2.142 (Type A). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Impedance Z0 | 100 Ω ± 15 Ω (1–100 MHz Cat5e Star-Quad)
Key data | Conductor | AWG 22/1 Solid (Ø 0.64 mm solid bare copper)
Key data | Shielding | SF/UTP (Foil+Cu) (Al/PET foil + ≥85 % tinned Cu braid)
Key data | FastConnect OD | 6.5 mm ± 0.2 (Fits RJ45 / M12 FC stripping tools)
Key data | Bandwidth | 100 MHz (Cat5e) (100BASE-TX real-time RT / IRT)
Key data | Min. bend radius | 4×D / 8×D (Fixed 4×D · pull-in 8×D)
Electrical | Characteristic impedance Z0 | 100 Ω ± 15 Ω (1 to 100 MHz)
Electrical | Max. DC loop resistance @ 20 °C | ≤ 115 Ω/km
Electrical | Mutual capacitance @ 1 kHz | ≈ 48 pF/m
Electrical | Velocity of propagation (VoP) | ≈ 65 % (0.65 c) · delay ≤ 530 ns/100m
Electrical | Attenuation (1 / 10 / 100 MHz) | 2.1 / 6.0 / 19.5 dB/100m
Electrical | Operating / test voltage | 300 V (UL) · 2.0 kV DC / 1.5 kV AC test
Thermal | Operating temp. (fixed PVC) | -40 °C to +80 °C
Thermal | Installation temperature | -20 °C to +60 °C
Mechanical | Min. bending radius (fixed / pull) | 4 × D fixed · 8 × D during pulling
Mechanical | Max. pulling tension | ≤ 100 N
Resistance | Oil & coolant resistance | EN 60811-404 (oil-resistant PVC & PUR
Resistance | Flame retardancy | IEC 60332-1-2 / UL 1685 CMG/PLTC
Standards | Primary specification | IEC 61156-5 / PNO Guideline 2.142 Type A
Standards | Transmission class | ISO/IEC 11801 Class D / Cat5e (100 MHz)
Identification | Core colours (Star-Quad) | White, Yellow, Blue, Orange
Identification | Outer sheath colour | RAL 6018 Yellow-Green (Black for outdoor PE)

## Construction
PROFINET Type A Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-a-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-5 / PNO Guideline 2.142 (Type A). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid bare copper conductor | AWG 22/1 (Ø 0.64 mm, 0.325 mm²) solid annealed bare copper per IEC 61156-5 | IEC 61156-5 / PNO Type A
2 | Core insulation (O2YS / 2YI1) | Low-permittivity PE / foam-skin PE insulation (Ø 1.50 mm) | PNO 2.142
3 | Star-Quad core lay-up | 4 cores twisted in Star-Quad (Pair 1: White/Blue, Pair 2: Yellow/Orange) with central | PNO 2.142 Star-Quad
4 | FastConnect inner bedding | Extruded thermoplastic inner sheath holding Star-Quad geometry for one-step FC stripping
5 | Static screen (Al/PET) | Aluminium-laminated polyester tape (100 % coverage, metal side out) | IEC 61156-5 SF/UTP
6 | EMC copper braid | Tinned copper wire braid, optical coverage ≥ 85 % | IEC 61156-5 SF/UTP
7 | Outer sheath (RAL 6018 green) | Flame-retardant PVC, halogen-free PUR (TMPU), FRNC/LSZH, or direct-burial PE | PNO 2.142
| PROFINET Type A FC PVC | Standard RAL 6018 green PVC FastConnect cable for indoor cable trays and cabinets.
| PROFINET Type A FC PUR / FRNC / PE | Oil-resistant PUR, halogen-free LSZH (FRNC), or black PE direct-burial fixed cable.

## Quality and supply
PROFINET Type A Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-a-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-5 / PNO Guideline 2.142 (Type A). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Impedance, NEXT & attenuation sweep — 1–100 MHz Cat5e / PNO Type A limits | 100 % of reels
Routine test | DC loop resistance & 2 kV dielectric — ≤ 115 Ω/km; 2.0 kV DC / 1 min without breakdown | 100 % of reels
Sample test | Coupling attenuation (EMC) — IEC 61156-5 Segregation Class c / d | Per production batch
Type test | Flame & oil resistance — IEC 60332-1-2 & EN 60811-404 | Type approval
Standard / approval | IEC 61156-5
Standard / approval | PNO Guideline 2.142
Standard / approval | UL / CSA CMG PLTC
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX PROFINET TYPE A FASTCONNECT
Supply | Delivery form: Non-returnable plywood reels or export drums
Supply | Standard reel lengths: 100 m · 305 m · 500 m · 1000 m
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP