## Request a quote
Request a quotation for PROFINET Type B
Share your protocol/frequency, jacket material (PVC, PUR, LSZH, FEP), and installation motion for PROFINET Type B.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/profinet-type-b-flexible-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
PROFINET Type B Flexible Cable – Dimensions & weights (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-b-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-6 / PNO Guideline 2.142 (Type B). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Conductor size | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| PROFINET Type B FC PVC 2×2×AWG22/7 | 2×2×AWG22/7 (PVC Flex) | AWG 22/7 (0.34 mm²) | 6.5 | 33 | 63 | 32 | Standard PROFINET Type B configurations
| PROFINET Type B FC PUR 2×2×AWG22/7 | 2×2×AWG22/7 (PUR Flex) | AWG 22/7 (0.34 mm²) | 6.5 | 33 | 61 | 32 | Standard PROFINET Type B configurations
| PROFINET Type B FC FRNC/LSZH 2×2×AWG22/7 | 2×2×AWG22/7 (FRNC/LSZH) | AWG 22/7 (0.34 mm²) | 6.5 | 33 | 65 | 32 | Standard PROFINET Type B configurations
| PROFINET Type B Marine SHF1 2×2×AWG22/7 | 2×2×AWG22/7 (Marine SHF1) | AWG 22/7 (0.34 mm²) | 6.6 | 34 | 66 | 33 | Standard PROFINET Type B configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per IEC 61156-6 / PNO Guideline 2.142 (Type B).

## Impedance, capacitance & attenu
PROFINET Type B Flexible Cable – Impedance, capacitance & attenuation (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-b-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-6 / PNO Guideline 2.142 (Type B). Values for your order are confirmed in the quotation.
Configuration | Impedance Z0 | Max. DC R @ 20 °C Ω/km | Mutual C pF/m ≈ | VoP % | Attenuation @ 20 °C dB/100m | Dielectric test V
2×2×AWG22/7 (PVC Flex) | 100 Ω | 120 | 50 | 65 | 2.5 @ 1 · 6.8 @ 10 · 21.8 @ 100 MHz | 2000
2×2×AWG22/7 (PUR Flex) | 100 Ω | 120 | 50 | 65 | 2.5 @ 1 · 6.8 @ 10 · 21.8 @ 100 MHz | 2000
2×2×AWG22/7 (FRNC/LSZH) | 100 Ω | 120 | 50 | 65 | 2.5 @ 1 · 6.8 @ 10 · 21.8 @ 100 MHz | 2000
2×2×AWG22/7 (Marine SHF1) | 100 Ω | 120 | 50 | 65 | 2.5 @ 1 · 6.8 @ 10 · 21.8 @ 100 MHz | 2000
Transmission values (characteristic impedance Z0, mutual capacitance, VoP, and attenuation) are measured at +20 °C per IEC 61156-6 / PNO Guideline 2.142 (Type B).

## Technical data
PROFINET Type B Flexible Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-b-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-6 / PNO Guideline 2.142 (Type B). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Impedance Z0 | 100 Ω ± 15 Ω (1–100 MHz Cat5e Star-Quad)
Key data | Conductor | AWG 22/7 Strand (7×0.25 mm tinned Cu (Ø 0.75 mm))
Key data | Shielding | SF/UTP (Foil+Cu) (Al/PET foil + ≥85 % tinned Cu braid)
Key data | Outer diameter | 6.5 mm ± 0.2 (FastConnect RJ45 / M12 compatible)
Key data | Bandwidth | 100 MHz (Cat5e) (PROFINET RT / IRT 100BASE-TX)
Key data | Min. bend radius | 5×D / 8×D (Fixed 5×D · flexing 8×D)
Electrical | Characteristic impedance Z0 | 100 Ω ± 15 Ω (1 to 100 MHz)
Electrical | Max. DC loop resistance @ 20 °C | ≤ 120 Ω/km
Electrical | Mutual capacitance @ 1 kHz | ≈ 50 pF/m
Electrical | Velocity of propagation (VoP) | ≈ 65 % (0.65 c) · delay ≤ 530 ns/100m
Electrical | Attenuation (1 / 10 / 100 MHz) | 2.5 / 6.8 / 21.8 dB/100m
Electrical | Operating / test voltage | 300 V / 600 V UL · 2.0 kV DC test
Thermal | Operating temp. (flexing / fixed) | -20 °C to +70 °C flexing · -40 °C to +80 °C
Thermal | Storage temperature | -40 °C to +80 °C
Mechanical | Min. bending radius (fixed | 5 × D fixed · 8 × D occasional flexing
Mechanical | Vibration & movement rating | PNO Type B machine vibration & occasional
Resistance | Oil & cutting fluid resistance | EN 60811-404 / UL Oil Res I & II
Resistance | Flame retardancy | IEC 60332-1-2 / UL VW-1 / CMG
Standards | Primary specification | IEC 61156-6 / PNO Guideline 2.142 Type B
Standards | Marine approvals (FRNC/SHF1 opt.) | DNV / ABS shipboard automation option
Identification | Core colours (Star-Quad) | White, Yellow, Blue, Orange
Identification | Outer sheath colour | RAL 6018 Yellow-Green

## Construction
PROFINET Type B Flexible Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-b-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-6 / PNO Guideline 2.142 (Type B). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 7-wire tinned copper conductor | AWG 22/7 (7×0.25 mm, 0.34 mm², Ø 0.75 mm) stranded tinned copper per IEC 61156-6 | IEC 61156-6 / PNO Type B
2 | Core insulation (PE / O2YS) | Low-capacitance polyethylene / foam-skin PE insulation (Ø 1.55 mm) | PNO 2.142
3 | Star-Quad core lay-up | 4 cores twisted in Star-Quad (White, Yellow, Blue, Orange) around central filler | PNO 2.142
4 | FastConnect inner bedding | Thermoplastic inner jacket maintaining circular 6.5 mm FastConnect stripping profile
5 | Static screen (Al/PET) | Aluminium-laminated polyester tape (100 % coverage) | IEC 61156-6 SF/UTP
6 | EMC copper braid | Tinned copper wire braid, optical coverage ≥ 85 % | IEC 61156-6 SF/UTP
7 | Outer sheath (RAL 6018 green) | Flexible oil-resistant PVC, halogen-free PUR (TMPU), or FRNC/LSZH compound | PNO 2.142 Type B
| PROFINET Type B FC PVC | Flexible RAL 6018 green PVC FastConnect cable for vibrating machinery and panel wiring.
| PROFINET Type B FC PUR / FRNC | Halogen-free PUR (UL Style 21198/20963) or shipboard/railway FRNC-LSZH flexible cable.

## Quality and supply
PROFINET Type B Flexible Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/profinet-type-b-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61156-6 / PNO Guideline 2.142 (Type B). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1–100 MHz network analyzer sweep — Z0 = 100 ± 15 Ω, NEXT & return loss per IEC 61156-6 | 100 % of reels
Routine test | DC loop resistance & 2 kV spark test — ≤ 120 Ω/km; 2.0 kV DC dielectric test | 100 % of reels
Sample test | Vibration & bending fatigue test — PNO 2.142 Type B conductor integrity | Per production batch
Type test | Flame & oil resistance — IEC 60332-1-2 & EN 60811-404 | Type approval
Standard / approval | IEC 61156-6
Standard / approval | PNO Guideline 2.142
Standard / approval | UL AWM 21198 / CMG
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX PROFINET TYPE B FLEXIBLE
Supply | Delivery form: Non-returnable plywood reels or export drums
Supply | Standard reel lengths: 100 m · 305 m · 500 m · 1000 m
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP