## Request a quote
Request a quotation for PROFIPLAST PBS-POOL
Specify core count (2×, 3G, 4G, or 5G), conductor cross-section (1.5 to 16 mm²), pool water sanitizer type (chlorine, bromine, or salt electrolysis), and
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/pbs-pool-chlorinated-water-resistant-permanent-submersion-swimming-pool-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
PROFIPLAST PBS-POOL Chlorinated-Water-Resistant Permanent – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/pbs-pool-chlorinated-water-resistant-permanent-submersion-swimming-pool-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / VDE 0285. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| PROFIPLAST PBS-POOL 2×1.5 | 2×1.5 | 1.5 | 8.6 | 29 | 102 | 34 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 2×2.5 | 2×2.5 | 2.5 | 10.2 | 48 | 145 | 41 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 2×4.0 | 2×4.0 | 4.0 | 11.8 | 77 | 205 | 47 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 2×6.0 | 2×6.0 | 6.0 | 13.4 | 115 | 275 | 54 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 3G1.5 | 3G1.5 | 1.5 | 9.4 | 43 | 125 | 38 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 3G2.5 | 3G2.5 | 2.5 | 11.1 | 72 | 180 | 44 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 4G1.5 | 4G1.5 | 1.5 | 10.4 | 58 | 155 | 42 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 4G2.5 | 4G2.5 | 2.5 | 12.2 | 96 | 225 | 49 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 4G4.0 | 4G4.0 | 4.0 | 14.2 | 154 | 325 | 57 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 4G6.0 | 4G6.0 | 6.0 | 16.2 | 230 | 445 | 65 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 5G1.5 | 5G1.5 | 1.5 | 11.4 | 72 | 190 | 46 | Standard PROFIPLAST PBS-POOL configurations
| PROFIPLAST PBS-POOL 5G2.5 | 5G2.5 | 2.5 | 13.5 | 120 | 275 | 54 | Standard PROFIPLAST PBS-POOL configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per EN 50525-2-21 AD8 / VDE 0285.

## Electrical & ampacity data
PROFIPLAST PBS-POOL Chlorinated-Water-Resistant Permanent – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/pbs-pool-chlorinated-water-resistant-permanent-submersion-swimming-pool-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / VDE 0285. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
2×1.5 | 13.633 | 22 | 19 | 80 | 2500
2×2.5 | 8.179 | 30 | 26 | 82 | 2500
2×4.0 | 5.074 | 40 | 34 | 84 | 2500
2×6.0 | 3.382 | 51 | 43 | 87 | 2500
3G1.5 | 13.633 | 22 | 19 | 80 | 2500
3G2.5 | 8.179 | 30 | 26 | 82 | 2500
4G1.5 | 13.633 | 22 | 19 | 80 | 2500
4G2.5 | 8.179 | 30 | 26 | 82 | 2500
4G4.0 | 5.074 | 40 | 34 | 84 | 2500
4G6.0 | 3.382 | 51 | 43 | 87 | 2500
5G1.5 | 13.633 | 22 | 19 | 80 | 2500
5G2.5 | 8.179 | 30 | 26 | 82 | 2500
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
PROFIPLAST PBS-POOL Chlorinated-Water-Resistant Permanent – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/pbs-pool-chlorinated-water-resistant-permanent-submersion-swimming-pool-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / VDE 0285. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (Up to 0.6/1 kV fixed submerged)
Key data | Water class | AD8 Submersion (Permanent immersion to 50 m depth)
Key data | Chlorine proof | ≤ 1.5–3.0 mg/L (Chlorine, bromine, ozone & salt water)
Key data | Conductor max. | +90 °C (air) (+40 °C continuous pool water)
Key data | Min. bend R | 4 × D / 6 × D (Fixed underwater / cleaner flexing)
Key data | Outer jacket | Non-staining (Hydrolysis-proof cross-linked elastomer)
Electrical | Rated voltage U0/U | 450/750 V AC (0.6/1 kV fixed)
Electrical | Routine AC test voltage | 2.5 kV rms / 5 min in water bath
Electrical | Wet insulation resistance | ≥ 1000 MΩ·km at +20 °C
Electrical | SELV / PELV compatibility | 12 V / 24 V AC/DC & 230/400 V AC
Electrical | Conductor stranding | EN 60228 Class 5 tinned copper
Electrical | Operating frequency | 50 / 60 Hz & DC
Thermal | Max. water temperature (AD8) | +40 °C continuous submersion
Thermal | Max. conductor temp. (in air) | +90 °C continuous
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Mobile ambient range | -25 °C to +60 °C
Thermal | Fixed ambient range | -40 °C to +80 °C
Thermal | Winter freeze resistance | Withstands ice formation in outdoor pools
Mechanical | Min. bend radius (fixed) | 4 × overall diameter (D)
Mechanical | Min. bend radius (mobile cleaner) | 6 × overall diameter (D)
Mechanical | Max. submersion depth (AD8) | Up to 50 m water head (5 bar)
Mechanical | Max. tensile pull on copper | 15 N/mm²
Mechanical | Surface friction | Low-drag non-marking smooth finish
Mechanical | Abrasion resistance | Resistant to ceramic tile & concrete
Resistance | Chlorinated pool water | Resistant up to 1.5–3.0 mg/L free Cl₂
Resistance | Brominated & ozonated water | Resistant to pool sanitizing chemicals
Resistance | Saltwater & thalassotherapy | 100 % seawater & brine resistant
Resistance | UV & outdoor sunlight | Colour-fast blue UV-stabilised jacket
Resistance | Liner & tile non-staining | Zero plasticizer migration on PVC liners
Resistance | RoHS / REACH status | Halogen-free / RoHS 3 compliant
Standards | Submersible design basis | EN 50525-2-21 Annex D/E (AD8)
Standards | Swimming pool installation norm | IEC 60364-7-702 / HD 60364-7-702
Standards | Underwater luminaire norm | EN 60598-2-18 swimming pool lights
Standards | Conductor standard | EN 60228 Class 5
Standards | Water submersion category | AD8 permanent submersion
Standards | Quality certification | EN 10204 3.1 test certificate
Identification | Core identification (≤ 5 cores) | HD 308 S2 colours (with G/Y in 3G–5G)
Identification | Core identification (≥ 7 cores) | White numbers on black cores + G/Y
Identification | Outer sheath colour | Pool blue (RAL 5015 / 5012) or black
Identification | Surface marking | TEBAOFLEX PBS-POOL AD8 450/750V [n×mm²]
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Lot number & year code

## Construction
PROFIPLAST PBS-POOL Chlorinated-Water-Resistant Permanent – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/pbs-pool-chlorinated-water-resistant-permanent-submersion-swimming-pool-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / VDE 0285. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible tinned copper conductor | Class 5 fine-stranded tin-coated annealed copper wire preventing capillary oxidation | EN 60228 Class 5
2 | Low-water-uptake EPR insulation | Special cross-linked ethylene-propylene elastomer (Type 3GI3 / EI4-AD8) with ultra-low | EN 50363-1
3 | Tight-pitch water-blocked lay-up | Cores stranded with short pitch and hydrophobic elastomeric interstices | VDE 0285 AD8
4 | Chlorine-resistant pool elastomer sheath | Cross-linked chlorine-, bromine-, and hydrolysis-resistant specialty elastomer compound | EN 50525-2-21 AD8
| PBS-POOL 2× / 3G (1.0–2.5 mm²) | Compact flexible cord for underwater SELV 12/24 V LED pool luminaires and commercial robotic pool cleaners.
| PBS-POOL 4G / 5G (1.5–16 mm²) | Three-phase + PE/N submersible feeder for wave machines, fountain pumps, and movable pool floors.

## Quality and supply
PROFIPLAST PBS-POOL Chlorinated-Water-Resistant Permanent – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/pbs-pool-chlorinated-water-resistant-permanent-submersion-swimming-pool-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / VDE 0285. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC water-bath dielectric voltage test — 2.5 kV rms for 5 minutes after 24 h water immersion | Every drum
Routine test | Tinned conductor DC resistance — Complies with EN 60228 Class 5 tinned limits at 20 °C | Every drum
Sample test | Chlorinated water immersion ageing — No surface chalking, swelling or cracking in chlorinated water at +40 °C | Per batch
Type test | Long-term AD8 gravimetric water absorption — Passes EN 50363 AD8 water uptake and wet IR stability test | Type approval
Standard / approval | EN 50525-2-21 AD8
Standard / approval | IEC 60364-7-702
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX PROFIPLAST PBS-POOL AD8 450/750V
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP