## Request a quote
Request a quotation for PV Wire UL 4703
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/pv-wire-solar-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
PV Wire UL 4703 Solar Cable – 2000 V dimensions & NEC ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/pv-wire-solar-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 4703 / CSA C22.2 No. 271 / NEC Article 690. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | AWG/kcmil & stranding | Nominal Ø mm | Weight ≈ kg/km | Max. DC R Ω/km | 90°C Air A | Series
| PV Wire 12 AWG 2kV | 12 AWG (3.31 mm²) 19W Tinned Cu | 6.15 | 54 | 5.43 | 40 | 2000 V Tinned Cu String Wire
| PV Wire 10 AWG 2kV | 10 AWG (5.26 mm²) 19W Tinned Cu | 6.76 | 74 | 3.41 | 55 | 2000 V Tinned Cu String Wire
| PV Wire 8 AWG 2kV | 8 AWG (8.37 mm²) 19W Tinned Cu | 8.08 | 115 | 2.14 | 80 | 2000 V Tinned Cu String Wire
| PV Wire 6 AWG 2kV | 6 AWG (13.3 mm²) 19W Tinned Cu | 9.04 | 165 | 1.35 | 105 | 2000 V DC Collector Feeders
| PV Wire 250 kcmil 2kV Cu | 250 kcmil (127 mm²) 37W Cu CT | 19.6 | 1340 | 0.141 | 455 | 2000 V DC Collector Feeders
| PV Wire 500 kcmil 2kV Al | 500 kcmil (253 mm²) AA-8000 Al CT | 25.4 | 1020 | 0.116 | 545 | 2000 V DC Collector Feeders
12 AWG and 10 AWG 2000 V outer diameters (6.15–6.76 mm) are calibrated to fit standard Stäubli MC4-Evo 2 and Amphenol H4 1500 V DC gland seals.

## Technical data
PV Wire UL 4703 Solar Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/pv-wire-solar-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 4703 / CSA C22.2 No. 271 / NEC Article 690. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | UL Subject 4703 (NEC Art. 690 grounded/ungrounded)
Key data | Voltage rating | 2000 V DC (Also 600 V & 1000 V DC tiers)
Key data | Size range | 14 AWG–750 kcmil (String (12–8) & Feeder (6–750))
Key data | Insulation | XLPE / Dual-Wall (+90 °C Wet / +105–125 °C Dry)
Key data | UV & Cold | 720 h + -40 °C (UL 1581 Sunlight & Cold Impact)
Key data | Burial rating | Direct Burial (Crush & impact qualified)
Electrical | Voltage ratings | 600 V · 1000 V · 2000 V DC (UL 4703)
Electrical | AC dielectric + spark test | 6.0–7.5 kV AC water-tank dielectric & 10–15 kV spark test
Electrical | Max. DC resistance @ 20 °C | 5.43 Ω/km (12 AWG) · 3.41 Ω/km (10 AWG) · 2.14 Ω/km (8 AWG)
Electrical | Long-term wet IR | UL 44 / RHW-2 90 °C water immersion stability
Thermal | Wet / dry operating temp. | +90 °C Wet · +105 °C / +125 °C Dry (per UL 4703 print)
Thermal | Cold impact & cold bend | -40 °C cold impact & cold mandrel bend per UL 1581
Thermal | Short-circuit temperature | +250 °C (5 s)
Mechanical | XLPE insulation thickness | 75 mil / 1.91 mm (14–10 AWG 2kV) · 85 mil / 2.16 mm (8–2 AWG 2kV)
Mechanical | Min. bend radius | 5 × OD (unshielded single conductor)
Mechanical | Direct burial crush test | Passes UL 854 underground service-entrance crush & impact
Resistance | Sunlight UV resistance | 720-hour Carbon-Arc / Xenon-Arc weatherometer (≥ 80 % retention)
Resistance | Flame propagation | UL 1581 VW-1 vertical flame & IEEE 1202 / FT4 (1/0 AWG+ CT)
Resistance | Ammonia & rodent options | Available with anti-termite/rodent nylon or bronze-tape barrier
Standards | North American PV std | UL 4703 · Dual-rated UL 44 RHW-2 / UL 854 USE-2
Standards | Electrical code | NFPA 70 (NEC) Article 690.31(C)(1)
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Surface print legend | SUN RES · -40C · DIRECT BURIAL · PV WIRE · 2000V · 90C WET · VW-1
Identification | Insulation colours | Black, Red (DC+), White (Grounded), Green (EGC)
Identification | Customs tariff (HS) | 8544.4993

## Construction
PV Wire UL 4703 Solar Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/pv-wire-solar-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 4703 / CSA C22.2 No. 271 / NEC Article 690. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned/bare copper (or AA-8000 Al) conductor | 19- to 133-strand tinned/bare annealed copper (14–2 AWG string/whip) or Class B compressed copper / AA-8000 aluminum (1/0 AWG–750 kcmil) | ASTM B3 / B8 / B33 / B800 compliant
2 | Heavy-wall cross-linked polyethylene (XLPE) dielectric | 75 mil (1.90 mm) to 140 mil (3.56 mm) thermoset XLPE (single-layer or co-extruded dual-layer with colour skin)
3 | Sunlight-, moisture- & flame-resistant outer XLPE skin | UV-stabilized Black (2.5 % carbon black), Red or White VW-1 flame-retardant XLPE outer surface
| PV Wire 12 / 10 / 8 AWG (2000 V Tinned Cu) | Flexible stranded tinned copper string & whip wire compatible with MC4 / Amphenol H4 1500 V connectors
| PV Wire 6 AWG to 750 kcmil (2000 V Cu / Al) | Direct-burial 2000 V DC combiner-to-inverter collection feeder (1/0 AWG and larger CT Rated for cable tray)

## Quality and supply
PV Wire UL 4703 Solar Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/pv-wire-solar-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 4703 / CSA C22.2 No. 271 / NEC Article 690. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 6.0–7.5 kV AC water-tank dielectric & 15 kV spark test — Zero breakdown and insulation resistance above UL 4703 minimum | Every manufactured reel
Type test | 720-hour UV weatherometer, -40 °C cold impact & VW-1 flame test — ≥ 80 % tensile/elongation retention after 720 h UV and zero -40 °C cracks | UL 4703 listing test
Type test | UL 854 Direct Burial crush & impact resistance test — Survives underground stone crush and impact loading without shorting | UL 4703 listing test
Standard / approval | UL 4703 Listed PV Wire
Standard / approval | UL 44 RHW-2 / UL 854 USE-2
Standard / approval | NEC Art. 690 & CSA C22.2 No. 271
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) PV WIRE 10 AWG 2000V 90C WET 105C DRY SUN RES -40C DIRECT BURIAL VW-1
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP