## Request a quote
Request a quotation for PVC/PVC UL/CSA 600V/1000V Torsion
Share core count × cross-section (mm² or AWG), screened/unscreened build, required torsion rating (±100°/m to ±450°/0.5m), minimum temperature (−40 or −50 °C) and length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/pvc-pvc-ul-csa-600v-1000v-torsion-wind-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
PVC/PVC UL/CSA 600 V / 1,000 V & VDE Cold-Modified (±150°/m) Torsion-R – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/pvc-pvc-ul-csa-600v-1000v-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Max. pulling kN ≈ | Min. bend R mm | Series
| PVC/PVC UL/CSA 600V/10 7G1.5 mm² | 7G1.5 mm² (or 7C × 16 AWG) | IEC 60228 Class 5/6 / Class K Cu | 11.4 | 215 | 2.4 | 70 | PVC/PVC UL/CSA 600V/1000V Torsion Construction Schedule (−40…+90 °C)
| PVC/PVC UL/CSA 600V/10 12G1.5 mm² | 12G1.5 mm² (or 12C × 16 AWG) | IEC 60228 Class 5/6 / Class K Cu | 14.8 | 345 | 4.1 | 90 | PVC/PVC UL/CSA 600V/1000V Torsion Construction Schedule (−40…+90 °C)
| PVC/PVC UL/CSA 600V/10 18G2.5 mm² | 18G2.5 mm² (or 18C × 14 AWG) | IEC 60228 Class 5/6 / Class K Cu | 19.6 | 680 | 9.8 | 120 | PVC/PVC UL/CSA 600V/1000V Torsion Construction Schedule (−40…+90 °C)
Custom conductor cross-sections, core counts, pre-lugged tower kits and drum lengths available per UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification.

## Electrical & thermal parameters
PVC/PVC UL/CSA 600 V / 1,000 V & VDE Cold-Modified (±150°/m) Torsion-R – Electrical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/pvc-pvc-ul-csa-600v-1000v-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ Ω/km | Rating / Impedance | Operating temp.
7G1.5 mm² (or 7C × 16 AWG) | 13.3 | 600 V / 1,000 V (18 A) | −40…+90 °C
12G1.5 mm² (or 12C × 16 AWG) | 13.3 | 600 V / 1,000 V (16 A) | −40…+90 °C
18G2.5 mm² (or 18C × 14 AWG) | 7.98 | 600 V / 1,000 V (24 A) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, AC high-voltage spark/dielectric and dimensional verification.

## Technical data
PVC/PVC UL/CSA 600 V / 1,000 V & VDE Cold-Modified (±150°/m) Torsion-R – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/pvc-pvc-ul-csa-600v-1000v-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 600 V / 1,000 V (Tested per UL AWM 1000V / CSA / VDE)
Key data | Operating temp. | −40…+90 °C (Cold-climate & nacelle wind service)
Key data | Min. bend radius | 6 × OD (Drip-loop, hub & tower routing)
Key data | Core / conductor | Class 5 / Class (Extra-flexible plain copper conductors)
Key data | Outer protection | Black Oil/Cold/U (Engineered for ±150°/m yaw drip-loop tor)
Key data | Standard | UL AWM 1000V / C (UL 758 AWM 600 V/1,000 V, CSA C22.2 No. )
Electrical | Rated voltage / operating system | 600 V / 1,000 V (UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification)
Electrical | Core / conductor construction | Class 5 / Class 6 Bare Copper (2-37 Cores, 0.5-70 mm²) — Extra-flexible plain copper conductors
Electrical | Primary dielectric / insulation | Cold-Modified PVC Core Insulation (UL/CSA & VDE) — Number-coded modified PVC rated 600 V / 1,000 V
Thermal | Continuous operating temperature | −40…+90 °C (wind turbine nacelle, hub & tower duty)
Thermal | Low-temperature torsion & cold bend | Verified cold-flex and torsion endurance across −40…+90 °C per UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel cable drum
Mechanical | Outer jacket / sheath protection | Black Oil/Cold/UV Modified PVC Jacket (-40 °C) — Engineered for ±150°/m yaw drip-loop torsion
Mechanical | Minimum bending radius | 6 × OD
Mechanical | Intermediate screen / separator / core layer | Cold-Modified PVC Core Insulation (UL/CSA & VDE) — Number-coded modified PVC rated 600 V / 1,000 V
Resistance | Oil, grease, ozone & UV resistance | Resistant to wind turbine gearbox oil, hydraulic fluid, ozone and UV weathering per UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification
Resistance | Flame retardancy & smoke/halogen emission | Flame-retardant and environmental performance verified per UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification
Standards | Conductor & flame/test standards | IEC 60228 / IEC 60332-1-2 & -3 / UL 2277 WTTC / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | PVC/PVC UL/CSA 600V/1000V Torsion
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Black Oil/Cold/U)
Identification | Customs tariff (HS) | 8544.49 / 8544.60

## Construction
PVC/PVC UL/CSA 600 V / 1,000 V & VDE Cold-Modified (±150°/m) Torsion-R – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/pvc-pvc-ul-csa-600v-1000v-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 / Class 6 Bare Copper (2-37 Core | Extra-flexible plain copper conductors
2 | Cold-Modified PVC Core Insulation (UL/CS | Number-coded modified PVC rated 600 V / 1,000 V
3 | Black Oil/Cold/UV Modified PVC Jacket (- | Engineered for ±150°/m yaw drip-loop torsion
| PVC/PVC UL/CSA 600V/1000V Torsion — Standard Wind Turbine Execution | Built to UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification with class 5 / class 6 bare copper (2-37 cores, 0.5-70 mm²) and black oil/cold/uv modified pvc jacket (-40 °c)
| PVC/PVC UL/CSA 600V/1000V Torsion — Pre-Cut Tower / Drip-Loop Kit | Available on bulk export reels or pre-cut to turbine tower section and nacelle drip-loop lengths
| PVC/PVC UL/CSA 600V/1000V Torsion — Cold Torsion & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, conductor DC resistance & cold-torsion qualification report

## Quality and supply
PVC/PVC UL/CSA 600 V / 1,000 V & VDE Cold-Modified (±150°/m) Torsion-R – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/pvc-pvc-ul-csa-600v-1000v-torsion-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification) — DC resistance at 20 °C and insulation/sheath wall thickness within UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification limits | Every manufactured drum length
Routine test | AC high-voltage dielectric & insulation resistance test (UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification) — Zero dielectric breakdown and verified insulation resistance for 600 V / 1,000 V rating | Every manufactured drum length
Type test | Low-temperature drip-loop torsion, oil & flame qualification (UL 758 AWM 600 V/1,000 V, CSA C22.2 No. 210 & VDE 0285 Wind Torsion Specification) — Verified cold torsion cycle endurance, oil resistance and flame retardancy across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | UL AWM 1000V / CSA / VDE Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX PVC/PVC UL/CSA 600V/1000V Torsion UL AWM 1000V / CSA / VDE 600 V / 1,000 V CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel reels or pre-cut wind turbine tower & drip-loop kits
Supply | Standard lengths: 500 m, 1,000 m or custom cut-to-length nacelle drip-loop and tower section sets
Supply | MOQ: 100 m (standard configurations) · 300 m (custom wind builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP