## Request a quote
Request a quotation for Parallel Constant-Wattage Heating Cable
Application engineer · industrial heat-tracing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/parallel-constant-wattage-heating-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Parallel Constant-Wattage Heating Cable – Power, zone pitch, circuit length & dimensions (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/parallel-constant-wattage-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Model designation | Rated Vac | Output W/m | Bus wire mm² | Zone length m | Max circuit m | Max maintain °C | Max exposure °C | Width × Thick. mm | Mass ≈ kg/km
| 10RDP2-FEP · 230 V | 230 Vac | 10 | 2.5 | 1 | 220 | 150 | 200 | 9.6 × 6.4 | 145
| 15RDP2-FEP · 230 V | 230 Vac | 15 | 2.5 | 1 | 180 | 150 | 200 | 9.6 × 6.4 | 146
| 20RDP2-FEP · 230 V | 230 Vac | 20 | 2.5 | 1 | 155 | 150 | 200 | 9.6 × 6.4 | 148
| 30RDP2-FEP · 230 V | 230 Vac | 30 | 2.5 | 1 | 125 | 150 | 200 | 9.8 × 6.6 | 152
| 40RDP2-FEP · 230 V | 230 Vac | 40 | 2.5 | 0.75 | 108 | 150 | 200 | 9.8 × 6.6 | 155
| 50RDP2-FEP · 230 V | 230 Vac | 50 | 2.5 | 0.75 | 95 | 150 | 200 | 10.0 × 6.8 | 158
| 10HDP2-PFA · 230 V | 230 Vac | 10 | 3.3 | 1.2 | 255 | 205 | 250 | 10.4 × 7.0 | 172
| 20HDP2-PFA · 230 V | 230 Vac | 20 | 3.3 | 1 | 180 | 205 | 250 | 10.4 × 7.0 | 175
| 30HDP2-PFA · 230 V | 230 Vac | 30 | 3.3 | 1 | 145 | 205 | 250 | 10.6 × 7.2 | 178
| 40HDP2-PFA · 230 V | 230 Vac | 40 | 3.3 | 0.75 | 125 | 205 | 250 | 10.6 × 7.2 | 182
| 50HDP2-PFA · 230 V | 230 Vac | 50 | 3.3 | 0.75 | 110 | 205 | 250 | 10.8 × 7.4 | 186
| 60HDP2-PFA · 230 V | 230 Vac | 60 | 3.3 | 0.5 | 95 | 205 | 250 | 10.8 × 7.4 | 190
| 30HDP4-PFA · 400 V | 400 Vac | 30 | 3.3 | 1.5 | 250 | 205 | 250 | 10.6 × 7.2 | 180
| 50HDP4-PFA · 400 V | 400 Vac | 50 | 3.3 | 1.2 | 190 | 205 | 250 | 10.8 × 7.4 | 188
Cut only midway between contact node indentations; up to one trailing dead zone (0.5–1.5 m) at the end termination remains unheated.

## Maximum pipe maintenance temper
Parallel Constant-Wattage Heating Cable – Maximum pipe maintenance temperature vs linear output (HDP PFA series) (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/parallel-constant-wattage-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Model designation | Linear power W/m | Max pipe T for T4 (+135 °C class) | Max pipe T for T3 (+200 °C class) | Max pipe T for T2 (+300 °C class) | Power-off exposure °C
10HDP2-PFA | 10 | +115 °C | +180 °C | +205 °C | 250
20HDP2-PFA | 20 | +95 °C | +165 °C | +205 °C | 250
30HDP2-PFA | 30 | +75 °C | +145 °C | +195 °C | 250
40HDP2-PFA | 40 | +55 °C | +125 °C | +180 °C | 250
50HDP2-PFA | 50 | — (Use T3/T2) | +105 °C | +165 °C | 250
60HDP2-PFA | 60 | — (Use T3/T2) | +85 °C | +150 °C | 250
Constant-wattage trace heaters require active pipe temperature sensing and high-limit cut-off per IEC/IEEE 60079-30-2 to maintain T-class compliance.

## Technical data
Parallel Constant-Wattage Heating Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/parallel-constant-wattage-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Linear output | 10–60 W/m (Constant output independent of pipe T)
Key data | Maintain temp. | +150 to +205 °C (RDP +150 °C (FEP) · HDP +205 °C (PFA))
Key data | Max. exposure T | +200 to +250 °C (HDP PFA grade rated to +250 °C power-off)
Key data | Supply voltage | 230 / 400 Vac (Single-phase 230 V or 400 V phase-phase)
Key data | Bus conductors | 2 × 2.5–3.3 mm² (Heating zone pitch 0.5 m to 1.5 m)
Key data | Min. bend radius | 30 mm (Avoid bending directly on contact nodes)
Electrical | Rated supply voltage | 230 Vac single-phase & 400 Vac phase-to-phase
Electrical | Linear power output | 10, 15, 20, 30, 40, 50 & 60 W/m (constant)
Electrical | Cold-start inrush | Zero inrush current rise (1.0 × steady state)
Electrical | Dielectric withstand | 2.5 kV AC for 1 min (bus to metallic braid)
Thermal | Max. maintain temp. | RDP (FEP): +150 °C · HDP (PFA): +205 °C
Thermal | Max. exposure temp. | RDP: +200 °C · HDP: +250 °C (power off)
Thermal | Min. installation T | −60 °C (fluoropolymer FEP / PFA construction)
Thermal | Temperature class | T4 (+135 °C), T3 (+200 °C) or T2 (+300 °C)
Mechanical | Bus wire cross-section | 2 × 2.5 mm² (RDP) or 2 × 3.3 mm² / 12 AWG
Mechanical | Heating zone length | 0.5 m to 1.5 m between bus contact nodes
Mechanical | Min. bending radius | 30 mm (avoid bending on contact nodes)
Mechanical | Overlap rule | Do not overlap; maintain ≥ 25 mm clearance
Resistance | Flame retardance | IEC 60332-1-2 & UL VW-1 flame retardant
Resistance | Chemical resistance | Inert to strong acids, alkalis, oils & steam
Resistance | Water & ingress | Non-hygroscopic PFA/FEP wall; IP66/IP67 kits
Resistance | UV & weathering | Permanent UV & ozone immunity (FEP / PFA)
Standards | Applicable standards | IEC/IEEE 60079-30-1, IEC 62395-1 & IEEE 515
Standards | Temperature control | Requires thermostat / RTD + overtemp limiter
Standards | Earth fault device | 30 mA RCD / GFPD per IEC 60079-30-2
Standards | RoHS & REACH | RoHS 2011/65/EU & REACH compliant materials
Identification | Node marking | Surface indentation / print mark at each node
Identification | Sheath colours | Amber/Translucent Red (HDP PFA) · Blue (RDP)
Identification | Outer legend | TEBAOFLEX · RDP/HDP · W/m · Vac · Zone mark
Identification | Customs tariff (HS) | 8544.49 (or 8516.80 electric heating cables)

## Construction
Parallel Constant-Wattage Heating Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/parallel-constant-wattage-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Parallel tinned / nickel-plated copper bus wires | 2 × 2.5 mm² or 3.3 mm² (12 AWG) stranded tinned or nickel-plated copper bus conductors | IEC 60228 / ASTM B33 / B355
2 | Primary bus-wire insulation with zone notches | Melt-extruded FEP (RDP), PFA (HDP) or high-temp silicone bus insulation with staggered contact windows every 0.5–1.5 m | IEC 60079-30-1
3 | Spirally wound NiCr 80/20 resistance heating wire | Nickel-chromium (80/20 NiCr) resistance alloy filament helically wound and metallurgically bonded to alternating bus nodes | IEC 60079-30-1 / IEEE 515
4 | Inner fluoropolymer dielectric jacket | Extruded FEP or PFA inner electrical insulation barrier isolating the NiCr heating coil from the earth screen | IEC 60079-30-1
5 | Tinned-copper protective earthing braid | Closely woven tinned/nickel-plated copper braid (≥ 70 % coverage) for fault current return and mechanical armouring | IEC 60079-30-1 Clause 4.4
6 | Fluoropolymer (PFA / FEP) outer sheath | High-temperature, chemically inert extruded FEP (RDP +200 °C) or PFA (HDP +250 °C) outer protective jacket | IEC 60079-30-1 / IEEE 515
| RDP Series · FEP Insulated (10–50 W/m · 230 V / 400 V) | Maintain up to +150 °C · Max exposure +200 °C · 2.5 mm² SnCu bus + NiCr zone element + FEP insulation + SnCu braid + FEP outer jacket
| HDP Series · PFA Insulated (10–60 W/m · 230 V / 400 V) | Maintain up to +205 °C · Max exposure +250 °C · 3.3 mm² (12 AWG) NiCu bus + NiCr zone element + PFA insulation + NiCu/SnCu braid + PFA outer sheath

## Quality and supply
Parallel Constant-Wattage Heating Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/parallel-constant-wattage-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage withstand test — 2.5 kV RMS AC for 1 min between bus conductors and metallic earth braid | Every reel
Routine test | Zone resistance & linear wattage check — Linear output W/m and bus-to-element contact node continuity verified across all zones | Every reel
Sample test | Cold impact, deformation & mandrel bend test — Mechanical crush (1,500 N), cold impact at −60 °C and 30 mm mandrel flexing | Production lot
Type test | 250 °C fluoropolymer thermal aging & node cycling — Extended thermal cycling of welded NiCr contact nodes and PFA dielectric integrity | Type qualification
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · [RDP/HDP MODEL] · [W/m] · [230V/400V] · PFA/FEP · IEC/IEEE 60079-30-1 · NODE MARK
Supply | Delivery form: Continuous fluoropolymer-sheathed reels or pre-terminated sets
Supply | Lengths: Cut to length in multiples of the 0.5–1.5 m heating zone
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None