## Request a quote
Request a quotation for R-(N)TSCGEWÖU + FO
Application engineer · MV reeling & electro-optical cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/r-n-tscgewou-fo-6-10kv-electro-optical-medium-voltage-mining-reeling-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
R-(N)TSCGEWÖU + FO 6/10 kV Electro-Optical Reeling Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/r-n-tscgewou-fo-6-10kv-electro-optical-medium-voltage-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60794-1-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| R-(N)TSCGEWÖU 3×35 + 2×25/2 + 12FO 6/10 kV | 3×35 + 2×25/2 + 12×SM/MM FO | Class 5 tinned Cu + 12FO | 46.5 | 3080 | 2.1 | 465 | R-(N)TSCGEWÖU + FO Construction Schedule (-25 to +80 °C)
| R-(N)TSCGEWÖU 3×50 + 2×25/2 + 12FO 6/10 kV | 3×50 + 2×25/2 + 12×SM/MM FO | Class 5 tinned Cu + 12FO | 50.4 | 3740 | 3 | 505 | R-(N)TSCGEWÖU + FO Construction Schedule (-25 to +80 °C)
| R-(N)TSCGEWÖU 3×70 + 2×35/2 + 18FO 6/10 kV | 3×70 + 2×35/2 + 18×SM/MM FO | Class 5 tinned Cu + 18FO | 55.2 | 4690 | 4.2 | 555 | R-(N)TSCGEWÖU + FO Construction Schedule (-25 to +80 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per DIN VDE 0250-813 / IEC 60794-1-2.

## Electrical, optical & thermal p
R-(N)TSCGEWÖU + FO 6/10 kV Electro-Optical Reeling Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/r-n-tscgewou-fo-6-10kv-electro-optical-medium-voltage-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60794-1-2. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3×35 + 2×25/2 + 12×SM/MM FO | 0.565 | 6/10 kV (169 A) + 12F Optical | -25 to +80 °C
3×50 + 2×25/2 + 12×SM/MM FO | 0.393 | 6/10 kV (206 A) + 12F Optical | -25 to +80 °C
3×70 + 2×35/2 + 18×SM/MM FO | 0.277 | 6/10 kV (255 A) + 18F Optical | -25 to +80 °C
Every production length undergoes routine conductor DC resistance, high-voltage Spark/AC dielectric or OTDR continuity and dimensional verification.

## Technical data
R-(N)TSCGEWÖU + FO 6/10 kV Electro-Optical Reeling Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/r-n-tscgewou-fo-6-10kv-electro-optical-medium-voltage-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60794-1-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 6/10 kV (6/10 kV MV power + 12/18F optical data)
Key data | Operating temp. | -25 to +80 °C (Continuous mining & industrial duty)
Key data | Min. bend radius | 10 × OD (Fixed installation / dynamic routing)
Key data | Core / conductor | 3×35–120+2E+12FO (Class 5 tinned Cu + A-D(ZN)13Y 12FO)
Key data | Outer protection | 5GM5 Red CR (5GM3 inner + anti-torsion + 5GM5 CR)
Key data | Standard | VDE 0250-813 (DIN VDE 0250-813 / IEC 60794-1-2)
Electrical | Rated voltage / transmission duty | 6/10 kV (DIN VDE 0250-813 / IEC 60794-1-2)
Electrical | Core / conductor construction | Phase Conductors (3×50 mm²) — DIN VDE 0295 Class 5 flexible tinned copper + triple-extruded 3GI3 EPR
Electrical | Primary dielectric / buffering | Split Earth Cores (2×25/2 mm²) — Two tinned copper earth conductors with semiconductive covering in interstices
Thermal | Continuous operating temperature | -25 to +80 °C (mining & industrial service)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per DIN VDE 0250-813 / IEC 60794-1-2
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Outer Sheath (5GM5 Red) — Heavy-duty red crosslinked polychloroprene rubber outer jacket
Mechanical | Minimum bending radius | 10 × OD
Mechanical | Crush, impact & abrasion duty | Heavy-duty mining rock-cut, impact and tensile protection per DIN VDE 0250-813 / IEC 60794-1-2
Resistance | Flame retardancy & mine fire safety | Self-extinguishing / flame-retardant mining jacket per DIN VDE 0250-813 / IEC 60794-1-2
Resistance | Mine water, oil & chemical resistance | Resistant to acidic mine water, hydraulic oils and abrasion per DIN VDE 0250-813 / IEC 60794-1-2
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | DIN VDE 0250-813 / IEC 60794-1-2
Standards | Flame & environmental test standards | IEC 60332 / MSHA / EN 60794 / IEC 60228
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | R-(N)TSCGEWÖU + FO
Identification | Sheath colour & metre marking | Continuous metre-marked red mining outer sheath
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
R-(N)TSCGEWÖU + FO 6/10 kV Electro-Optical Reeling Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/r-n-tscgewou-fo-6-10kv-electro-optical-medium-voltage-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60794-1-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase Conductors (3×50 mm²) | DIN VDE 0295 Class 5 flexible tinned copper + triple-extruded 3GI3 EPR
2 | Split Earth Cores (2×25/2 mm²) | Two tinned copper earth conductors with semiconductive covering in interstices
3 | Fiber-Optic Module (A-D(ZN)13Y 12FO) | Crush-resistant optical unit in 3rd interstice with 12 SM/MM fibres
4 | 5GM3 Inner Sheath & Polyamide Braid | Black 5GM3 thermosetting inner sheath + polyamide anti-torsion braid
5 | Outer Sheath (5GM5 Red) | Heavy-duty red crosslinked polychloroprene rubber outer jacket
| R-(N)TSCGEWÖU + FO — Standard Mining Execution | Built to DIN VDE 0250-813 / IEC 60794-1-2 with phase conductors (3×50 mm²) and outer sheath (5gm5 red)
| R-(N)TSCGEWÖU + FO — Custom Drum Length & Gland Kit | Available in custom shaft/roadway drum lengths or pre-terminated assemblies
| R-(N)TSCGEWÖU + FO — Routine & Flame Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & flame test report

## Quality and supply
R-(N)TSCGEWÖU + FO 6/10 kV Electro-Optical Reeling Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/r-n-tscgewou-fo-6-10kv-electro-optical-medium-voltage-mining-reeling-cable/ ¦ Data revision 2026-10-24
Typical values for this cable type, based on DIN VDE 0250-813 / IEC 60794-1-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (DIN VDE 0250-813 / IEC 60794-1-2) — DC resistance at 20 °C / optical attenuation and outer diameter within DIN VDE 0250-813 / IEC 60794-1-2 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (DIN VDE 0250-813 / IEC 60794-1-2) — Zero dielectric breakdown and verified insulation resistance over full production length | Every manufactured drum length
Type test | Flame propagation, mechanical crush & thermal ageing qualification (DIN VDE 0250-813 / IEC 60794-1-2) — Verified flame retardancy, mechanical integrity and thermal endurance across -25 to +80 °C | Type qualification & periodic lot audit
Standard / approval | VDE 0250-813 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX R-(N)TSCGEWÖU + FO VDE 0250-813 6/10 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel mine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shaft/reeling lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP