## Request a quote
Request a quotation for RD-Y(St)Y
Application engineer · process instrumentation & Ex-i/Ex-d
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/rd-y-st-y-paired-screened-process-control-station-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
RD-Y(St)Y Bd PVC-Insulated Paired Electrostatic-Screened Process – Dimensions, construction & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rd-y-st-y-paired-screened-process-control-station-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0815. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Outer Ø ≈ mm | Weight ≈ kg/km | Min. bend R fixed mm | Series
| RD-Y(St)Y 1×2×0.5 | 1×2×0.5 mm² | 6.4 | 58 | 52 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 2×2×0.5 | 2×2×0.5 mm² | 9.2 | 112 | 74 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 4×2×0.5 | 4×2×0.5 mm² | 11.4 | 176 | 92 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 8×2×0.5 | 8×2×0.5 mm² | 14.8 | 295 | 118 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 12×2×0.5 | 12×2×0.5 mm² | 17.6 | 420 | 141 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 1×2×1.0 | 1×2×1.0 mm² | 7.6 | 86 | 61 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 2×2×1.0 | 2×2×1.0 mm² | 11 | 168 | 88 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 4×2×1.0 | 4×2×1.0 mm² | 13.5 | 264 | 108 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 8×2×1.0 | 8×2×1.0 mm² | 17.9 | 465 | 143 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 1×2×1.5 | 1×2×1.5 mm² | 8.5 | 114 | 68 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 4×2×1.5 | 4×2×1.5 mm² | 15.2 | 348 | 122 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
| RD-Y(St)Y 12×2×1.5 | 12×2×1.5 mm² | 23.4 | 860 | 187 | RD-Y(St)Y Standard Construction Schedule (300 V · −30…+70 °C)
Additional pair/triad/quad counts (up to 48 pairs) and blue Ex-i intrinsically safe outer sheaths available per DIN VDE 0815.

## Electrical parameters by conduc
RD-Y(St)Y Bd PVC-Insulated Paired Electrostatic-Screened Process – Electrical parameters by conductor cross-section (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rd-y-st-y-paired-screened-process-control-station-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0815. Values for your order are confirmed in the quotation.
Conductor size | Max. DC R₂₀ Ω/km | Mutual cap. ≈ nF/km | Inductance ≈ mH/km
0.50 mm² (7/0.30 mm · AWG 20) | 39 | 115 | 0.65
0.75 mm² (7/0.37 mm · AWG 18) | 26 | 120 | 0.62
1.00 mm² (7/0.43 mm · AWG 17) | 19.5 | 125 | 0.6
1.50 mm² (7/0.53 mm · AWG 16) | 13.3 | 135 | 0.58
2.50 mm² (7/0.67 mm · AWG 14) | 7.98 | 145 | 0.55
L/R ratio ≤ 25 µH/Ω (0.5–1.0 mm²) and ≤ 40 µH/Ω (1.5 mm²) for intrinsically safe Ex-i circuits.

## Technical data
RD-Y(St)Y Bd PVC-Insulated Paired Electrostatic-Screened Process – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/rd-y-st-y-paired-screened-process-control-station-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0815. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300 V (Per DIN VDE 0815)
Key data | Operating temp. | −30…+70 °C (Continuous thermal rating)
Key data | Min. bend radius | 7.5 × OD (Installed / fixed routing)
Key data | Conductor | bare & tinned (High-conductivity bare & tinned)
Key data | Outer layer | PVC outer sheath (Extruded PVC outer sheath RAL 7032)
Key data | Standard | DIN VDE 0815 (DIN VDE 0815)
Electrical | Rated voltage / duty | 300 V (DIN VDE 0815)
Electrical | Conductor construction | Stranded bare & tinned copper conductor — High-conductivity bare & tinned copper conductor per DIN VDE 0815
Electrical | Primary insulation / dielectric | PVC core insulation — Extruded PVC dielectric (individual core / group layer)
Thermal | Continuous operating temperature | −30…+70 °C per DIN VDE 0815
Thermal | Short-circuit / peak thermal limit | +160 °C to +250 °C (5 s adiabatic limit depending on dielectric class)
Thermal | Minimum installation temperature | −5 °C (thermoplastic) / −25 °C (cross-linked or elastomer) / −40 °C (metallic)
Mechanical | Outer protection / covering | PVC outer sheath RAL 7032 — Extruded PVC outer sheath RAL 7032 protective layer (continuous layer)
Mechanical | Minimum bending radius | 7.5 × OD (installed / static routing)
Mechanical | Layer count & geometry | 5 concentric/structural layers verified by cross-section inspection
Resistance | Environmental & chemical durability | Engineered for industrial service in accordance with DIN VDE 0815
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing product standard | DIN VDE 0815
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | RD-Y(St)Y
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 7614.10

## Construction
RD-Y(St)Y Bd PVC-Insulated Paired Electrostatic-Screened Process – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/rd-y-st-y-paired-screened-process-control-station-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0815. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded bare & tinned copper conductor | High-conductivity bare & tinned copper conductor per DIN VDE 0815 | DIN VDE 0815
2 | PVC core insulation | Extruded PVC dielectric (individual core / group layer) | DIN VDE 0815
3 | Polyester binder | Helically applied polyester binder | DIN VDE 0815
4 | Al/polyester overall screen | Al/polyester overall screen metallic electromagnetic screen (lapped tape) | DIN VDE 0815
5 | PVC outer sheath RAL 7032 | Extruded PVC outer sheath RAL 7032 protective layer (continuous layer) | DIN VDE 0815
| RD-Y(St)Y — Standard Execution | Built to DIN VDE 0815 with stranded bare & tinned copper conductor and pvc outer sheath ral 7032
| RD-Y(St)Y — Custom Cross-Sections | Full range of metric mm² and AWG/kcmil conductor sizes per DIN VDE 0815
| RD-Y(St)Y — Export Drum Supply | Supplied with EN 10204 3.1 routine dielectric & conductor resistance test certificate

## Quality and supply
RD-Y(St)Y Bd PVC-Insulated Paired Electrostatic-Screened Process – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/rd-y-st-y-paired-screened-process-control-station-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN VDE 0815. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (DIN VDE 0815) — DC resistance at 20 °C and geometry within DIN VDE 0815 class limits | Every manufactured drum / spool
Routine test | Routine dielectric / spark / structural integrity test (DIN VDE 0815) — Zero breakdown or structural defect over full production length | Every manufactured drum / spool
Type test | Thermal aging, mechanical & material qualification (DIN VDE 0815) — Full compliance with DIN VDE 0815 across −30…+70 °C | Type qualification & periodic sample audit
Standard / approval | DIN VDE 0815 Compliant
Standard / approval | EN 10204 3.1 Routine Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX RD-Y(St)Y <size> DIN VDE 0815 300 V CE
Supply | Delivery form: Non-returnable fumigated wooden drums or precision DIN spools
Supply | Standard lengths: 500 m · 1000 m · 2000 m drums (custom cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP