## Request a quote
Request a quotation for RFOU-VFD P18 & RU-VFD 0.6/1-1.8/3 KV (NEK 606)
Share thruster/pump motor kW, system voltage (0.6/1 kV, 1.8/3 kV or 2,000 V), phase cross-section and EMC gland requirements.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/rfou-vfd-p18-ru-vfd-0-6-1-1-8-3-kv-nek-606/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
RFOU-VFD P18 & RU-VFD 0.6/1–1.8/3 kV NEK 606 Symmetrical 3+3E Offshore – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rfou-vfd-p18-ru-vfd-0-6-1-1-8-3-kv-nek-606/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| RFOU-VFD P18 3×35+3G6 VFD | 3 × 35 + 3G6 mm² (3+3E EMC) | IEC 60228 Class 2/5 Cu/SnCu | 29.4 | 1760 | 15.8 | 235 | RFOU-VFD P18 & RU-VFD 0.6/1-1.8/3 KV (NEK 606) Construction Schedule (−40…+90 °C)
| RFOU-VFD P18 3×70+3G10 VFD | 3 × 70 + 3G10 mm² (3+3E EMC) | IEC 60228 Class 2/5 Cu/SnCu | 37.8 | 3190 | 31.5 | 305 | RFOU-VFD P18 & RU-VFD 0.6/1-1.8/3 KV (NEK 606) Construction Schedule (−40…+90 °C)
| RFOU-VFD P18 3×120+3G16 VFD | 3 × 120 + 3G16 mm² (3+3E EMC) | IEC 60228 Class 2/5 Cu/SnCu | 46.5 | 5120 | 54 | 375 | RFOU-VFD P18 & RU-VFD 0.6/1-1.8/3 KV (NEK 606) Construction Schedule (−40…+90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD.

## Electrical, optical & thermal p
RFOU-VFD P18 & RU-VFD 0.6/1–1.8/3 kV NEK 606 Symmetrical 3+3E Offshore – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rfou-vfd-p18-ru-vfd-0-6-1-1-8-3-kv-nek-606/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 35 + 3G6 mm² (3+3E EMC) | 0.524 | 0.6/1 kV – 1.8/3 kV (138 A VFD) | −40…+90 °C
3 × 70 + 3G10 mm² (3+3E EMC) | 0.268 | 0.6/1 kV – 1.8/3 kV (215 A VFD) | −40…+90 °C
3 × 120 + 3G16 mm² (3+3E EMC) | 0.153 | 0.6/1 kV – 1.8/3 kV (305 A VFD) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
RFOU-VFD P18 & RU-VFD 0.6/1–1.8/3 kV NEK 606 Symmetrical 3+3E Offshore – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/rfou-vfd-p18-ru-vfd-0-6-1-1-8-3-kv-nek-606/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV – 1.8/3 (Tested per NEK TS 606 P18 / IEC 60092-35)
Key data | Operating temp. | −40…+90 °C (Continuous shipboard & offshore service)
Key data | Min. bend radius | 8 × OD (Marine tray, bulkhead & deck routing)
Key data | Core / conductor | Tinned Copper Ph (1.8/3 kV corona-resistant EPR insulation)
Key data | Outer protection | SHF2-MUD Offshor (NEK TS 606 oil- and ester-mud resistant )
Key data | Standard | NEK TS 606 P18 / (NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD )
Electrical | Rated voltage / transmission duty | 0.6/1 kV – 1.8/3 kV (NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD)
Electrical | Core / conductor construction | Tinned Copper Phase Cores (3×95 mm² EPR) — 1.8/3 kV corona-resistant EPR insulation withstanding PWM voltage spikes
Electrical | Primary dielectric / buffering | 3+3E Symmetrical Split Earth (3G16 mm²) — Three interstitial earth conductors balancing common-mode currents
Thermal | Continuous operating temperature | −40…+90 °C (shipboard & offshore duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | SHF2-MUD Offshore Outer Sheath (P18) — NEK TS 606 oil- and ester-mud resistant cross-linked elastomer jacket
Mechanical | Minimum bending radius | 8 × OD
Mechanical | Armour, screen & mechanical duty | Dual EMC Screen (Copper Tape + TCWB) — 100% copper-backed tape + tinned copper wire braid over SHF2 inner sheath
Resistance | Flame, fire & smoke performance | Qualified for marine flame-retardance and low-smoke zero-halogen / fire safety per NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD
Resistance | Oil, drilling mud & seawater resistance | Resistant to marine fuel/lube oils, salt mist and offshore fluids per NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD
Standards | Environmental & test standards | IEC 60228 / IEC 60332-3-22 / IEC 60754 / IEC 61034 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | RFOU-VFD P18 & RU-VFD 0.6/1-1.8/3 KV (NEK 606)
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (SHF2-MUD Offshor)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
RFOU-VFD P18 & RU-VFD 0.6/1–1.8/3 kV NEK 606 Symmetrical 3+3E Offshore – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/rfou-vfd-p18-ru-vfd-0-6-1-1-8-3-kv-nek-606/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned Copper Phase Cores (3×95 mm² EPR) | 1.8/3 kV corona-resistant EPR insulation withstanding PWM voltage spikes
2 | 3+3E Symmetrical Split Earth (3G16 mm²) | Three interstitial earth conductors balancing common-mode currents
3 | Dual EMC Screen (Copper Tape + TCWB) | 100% copper-backed tape + tinned copper wire braid over SHF2 inner sheath
4 | SHF2-MUD Offshore Outer Sheath (P18) | NEK TS 606 oil- and ester-mud resistant cross-linked elastomer jacket
| RFOU-VFD P18 & RU-VFD 0.6/1-1.8/3 KV (NEK 606) — Standard Shipboard & Offshore Execution | Built to NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD with tinned copper phase cores (3×95 mm² epr) and shf2-mud offshore outer sheath (p18)
| RFOU-VFD P18 & RU-VFD 0.6/1-1.8/3 KV (NEK 606) — Custom Drum Length & Gland Kit | Available in custom continuous shipboard/offshore drum lengths or with marine EMC cable glands
| RFOU-VFD P18 & RU-VFD 0.6/1-1.8/3 KV (NEK 606) — Class & Routine Test Certified | Supplied with EN 10204 3.1 routine dielectric, conductor resistance & flame/fire test report

## Quality and supply
RFOU-VFD P18 & RU-VFD 0.6/1–1.8/3 kV NEK 606 Symmetrical 3+3E Offshore – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/rfou-vfd-p18-ru-vfd-0-6-1-1-8-3-kv-nek-606/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD) — DC resistance at 20 °C / optical attenuation and outer diameter within NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD) — Zero dielectric breakdown and verified insulation resistance for 0.6/1 kV – 1.8/3 kV rating | Every manufactured drum length
Type test | Flame, fire integrity, oil/mud & mechanical qualification (NEK TS 606 Code P18 (RFOU-VFD) & RU-VFD / IEC 60092-353 SHF2-MUD) — Verified flame/fire performance, fluid resistance and thermal stability across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | NEK TS 606 P18 / IEC 60092-353 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX RFOU-VFD P18 & RU-VFD 0.6/1-1.8/3 KV (NEK 606) NEK TS 606 P18 / IEC 60092-353 0.6/1 kV – 1.8/3 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel marine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shipboard/offshore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP