## Request a quote
Request a quotation for RG7H1OR
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/rg7h1or-three-core-hepr-insulated-mv-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
RG7H1OR Three-Core HEPR-Insulated MV Cable – 12/20 kV 3-core dimensions & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1or-three-core-hepr-insulated-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2 / CEI UNEL 35375. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | CEI designation | Conductors & screen | Outer Ø ≈ mm | Weight ≈ kg/km | Air 30°C A | Buried 20°C A | Series
| RG7H1OR 3×25/16 12/20kV | 3 × 25 mm² Cl.2 Cu + H16 screen | 46.5 | 2450 | 152 | 146 | 12/20 kV RG7H1OR Three-Core Screened MV Cables
| RG7H1OR 3×35/16 12/20kV | 3 × 35 mm² Cl.2 Cu + H16 screen | 49.2 | 2860 | 182 | 172 | 12/20 kV RG7H1OR Three-Core Screened MV Cables
| RG7H1OR 3×50/16 12/20kV | 3 × 50 mm² Cl.2 Cu + H16 screen | 52 | 3340 | 218 | 204 | 12/20 kV RG7H1OR Three-Core Screened MV Cables
| RG7H1OR 3×70/16 12/20kV | 3 × 70 mm² Cl.2 Cu + H16 screen | 56.2 | 4120 | 268 | 246 | 12/20 kV RG7H1OR Three-Core Screened MV Cables
| RG7H1OR 3×95/16 12/20kV | 3 × 95 mm² Cl.2 Cu + H16 screen | 60.5 | 5060 | 324 | 292 | 12/20 kV RG7H1OR Three-Core Screened MV Cables
| RG7H1OR 3×150/16 12/20kV | 3 × 150 mm² Cl.2 Cu + H16 screen | 67.2 | 6850 | 420 | 368 | 12/20 kV RG7H1OR Three-Core Screened MV Cables
Also available in 6/10 kV, 8.7/15 kV and 18/30 kV voltage classes up to 3×240 / 3×300 mm².

## Technical data
RG7H1OR Three-Core HEPR-Insulated MV Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1or-three-core-hepr-insulated-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2 / CEI UNEL 35375. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | CEI 20-13 / IEC (Three-core screened MV cable)
Key data | Voltage classes | 8.7/15 to 18/30 (Also 3.6/6 kV & 6/10 kV)
Key data | Cross-sections | 3 × 25 to 300 mm (Class 2 compacted red Cu ('R'))
Key data | Insulation | G7 HEPR (+105 °C (High-modulus EPR (+250 °C SC))
Key data | Phase screens | 3 × H1 Copper Sc (Radial field on each phase core)
Key data | Outer sheath | Red PVC Type Rz (CEI 20-22 II Cat A flame)
Electrical | Rated voltage tiers (Uo/U) | 6/10 kV · 8.7/15 kV · 12/20 kV · 18/30 kV (Umax up to 36 kV)
Electrical | Routine AC test voltage | 21 kV (6/10) · 30.5 kV (8.7/15) · 42 kV (12/20) · 63 kV (18/30) for 5 min
Electrical | Partial discharge limit | ≤ 5 pC at 1.73 × Uo on every individual phase core
Electrical | Max. DC resistance @ 20 °C | 0.524 Ω/km (35) · 0.387 Ω/km (50) · 0.193 Ω/km (95) · 0.124 Ω/km (150)
Thermal | Continuous conductor temp. | +105 °C continuous operation (G7 HEPR)
Thermal | Emergency overload temp. | +140 °C
Thermal | Short-circuit temperature | +250 °C (max. 5 s)
Mechanical | G7 HEPR wall thickness | 3.6 mm (8.7/15 kV) · 4.5 mm (12/20 kV) · 6.5 mm (18/30 kV)
Mechanical | Min. bend radius | 12 × overall cable OD (fixed installation)
Mechanical | Short-circuit electrodynamic | Self-contained 3-core lay resists phase-to-phase short-circuit forces
Resistance | Bunched flame propagation | CEI 20-22 II & IEC 60332-3-22 Cat A vertical tray fire test
Resistance | Reduced halogen emission | CEI 20-37 / EN 60754-1: ≤ 18 % HCl (Rz PVC compound)
Resistance | Water & environmental | Suitable for indoor trays, outdoor pipe racks, ducts & buried trenches
Standards | Italian & IEC standards | CEI 20-13 · CEI UNEL 35375 · IEC 60502-2
Standards | Ampacity tables | CEI UNEL 35027 (+105 °C three-core MV tables)
Standards | RoHS, REACH & CE | 2011/65/EU RoHS 2, REACH & CE compliant
Identification | CEI code breakdown | R=Cu · G7=HEPR 105°C · H1=Cu screen · O=3-core · R=Red PVC Rz sheath
Identification | Phase identification | Numbered/coloured tapes under each H1 copper screen (1, 2, 3)
Identification | Customs tariff (HS) | 8544.6010

## Construction
RG7H1OR Three-Core HEPR-Insulated MV Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1or-three-core-hepr-insulated-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2 / CEI UNEL 35375. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3 × Class 2 compacted circular red copper conductors ('R') | Stranded compacted annealed plain copper per CEI EN 60228 Class 2 (3 × 25 mm² to 3 × 300 mm²)
2 | Triple-extruded inner & cold-strippable outer semicon screens | Thermoset semiconducting conductor screen and easy-peel outer insulation screen on each phase core
3 | +105 °C G7 High-Modulus HEPR dielectric insulation | Hard-grade Ethylene Propylene Rubber compound Type G7 per CEI 20-11 (+105 °C continuous, +250 °C short-circuit)
4 | 3 × Individual H1 copper tape/wire screens + fillers ('O') | Helically lapped annealed red copper tape or concentric wires on each phase core (total screen ≥ 16–25 mm²), laid up with fillers ('O')
5 | Overall Red flame-retardant PVC outer sheath ('R', Type Rz) | Flame-retardant polyvinyl chloride compound Type Rz per CEI 20-11 in Red (RAL 3000)
| RG7H1OR 8.7/15 kV (3×25 to 3×240 mm²) | 8.7/15 kV (Umax 17.5 kV, 3.6 mm G7 wall) three-core screened MV cable for 15 kV industrial distribution and RMU loops
| RG7H1OR 12/20 kV (3×35 to 3×300 mm²) | 12/20 kV (Umax 24 kV, 4.5 mm G7 wall) three-core screened MV cable for 20 kV plant substations and large MV motors
| RG7H1OR 18/30 kV (3×50 to 3×240 mm²) | 18/30 kV (Umax 36 kV, 6.5 mm G7 wall) three-core screened MV cable for 30/33 kV industrial and renewable feeders

## Quality and supply
RG7H1OR Three-Core HEPR-Insulated MV Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1or-three-core-hepr-insulated-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2 / CEI UNEL 35375. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 3.5 × Uo AC voltage test (42 kV on 12/20 kV) & 3-phase PD test — Zero breakdown for 5 min and PD ≤ 5 pC at 1.73 × Uo on all 3 cores | Every manufactured drum
Type test | G7 HEPR high-modulus hot-set, 125/170 kV BIL impulse & thermal cycling — Meets CEI 20-13 / IEC 60502-2 dielectric and mechanical limits | Type qualification
Sample test | CEI 20-22 II Cat A bunched vertical flame propagation test — Self-extinguishes within 2.5 m char limit under Cat A fuel load | Per production batch
Standard / approval | CEI 20-13 & IEC 60502-2
Standard / approval | CEI 20-22 II Cat A Flame
Standard / approval | RoHS 2, REACH & CE
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX RG7H1OR 12/20kV CEI 20-13 CEI 20-22 II
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP