## Request a quote
Request a quotation for RG7H1OZR
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/rg7h1ozr-three-core-screened-armoured-mv-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
RG7H1OZR Three-Core Screened Armoured MV Cable – 12/20 kV 3-core SWA dimensions & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1ozr-three-core-screened-armoured-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | CEI designation | Conductors, screen & SWA | Outer Ø ≈ mm | Weight ≈ kg/km | Air 30°C A | Buried 20°C A | Series
| RG7H1OZR 3×25/16 12/20kV | 3×25 mm² + H16 + 2.0 mm SWA | 53.5 | 4120 | 150 | 145 | 12/20 kV RG7H1OZR Three-Core Screened & Steel-Armoured MV
| RG7H1OZR 3×35/16 12/20kV | 3×35 mm² + H16 + 2.0 mm SWA | 56.2 | 4650 | 180 | 170 | 12/20 kV RG7H1OZR Three-Core Screened & Steel-Armoured MV
| RG7H1OZR 3×50/16 12/20kV | 3×50 mm² + H16 + 2.5 mm SWA | 60.2 | 5580 | 215 | 202 | 12/20 kV RG7H1OZR Three-Core Screened & Steel-Armoured MV
| RG7H1OZR 3×70/16 12/20kV | 3×70 mm² + H16 + 2.5 mm SWA | 64.5 | 6540 | 264 | 244 | 12/20 kV RG7H1OZR Three-Core Screened & Steel-Armoured MV
| RG7H1OZR 3×95/16 12/20kV | 3×95 mm² + H16 + 2.5 mm SWA | 68.8 | 7680 | 320 | 288 | 12/20 kV RG7H1OZR Three-Core Screened & Steel-Armoured MV
| RG7H1OZR 3×150/16 12/20kV | 3×150 mm² + H16 + 2.5 mm SWA | 75.8 | 9750 | 414 | 364 | 12/20 kV RG7H1OZR Three-Core Screened & Steel-Armoured MV
Because the magnetic fields of all three phases cancel inside the 3-core assembly, ferromagnetic galvanized steel wire armour ('Z') can be used without eddy-current heating.

## Technical data
RG7H1OZR Three-Core Screened Armoured MV Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1ozr-three-core-screened-armoured-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | CEI 20-13 / IEC (Screened & armoured 3-core MV)
Key data | Voltage classes | 6/10 to 18/30 kV (6/10, 8.7/15, 12/20, 18/30 kV)
Key data | Cross-sections | 3 × 25 to 240 mm (Class 2 compacted red Cu ('R'))
Key data | Insulation | G7 HEPR (+105 °C (High-modulus EPR (+250 °C SC))
Key data | Screen + Armour | 3×H1 Cu + Z SWA (Radial field + steel wire armour)
Key data | Outer sheath | Red PVC Type Rz (CEI 20-22 II Cat A flame)
Electrical | Rated voltage tiers (Uo/U) | 6/10 kV · 8.7/15 kV · 12/20 kV · 18/30 kV (Umax up to 36 kV)
Electrical | Routine AC test voltage | 21 kV (6/10) · 30.5 kV (8.7/15) · 42 kV (12/20) · 63 kV (18/30) for 5 min
Electrical | Partial discharge limit | ≤ 5 pC at 1.73 × Uo on every phase core
Electrical | Max. DC resistance @ 20 °C | 0.524 Ω/km (35) · 0.387 Ω/km (50) · 0.193 Ω/km (95) · 0.124 Ω/km (150)
Thermal | Continuous conductor temp. | +105 °C continuous operation (G7 HEPR)
Thermal | Emergency overload temp. | +140 °C
Thermal | Short-circuit temperature | +250 °C (max. 5 s)
Mechanical | G7 HEPR wall + Armour | 4.5 mm G7 wall (12/20 kV) + 2.0/2.5 mm galvanized round steel wires
Mechanical | Min. bend radius | 15 × overall cable OD (during pulling) · 12 × OD (fixed)
Mechanical | Vertical shaft support | Round steel wire armour supports vertical drop weights in mine shafts
Resistance | Bunched flame propagation | CEI 20-22 II & IEC 60332-3-22 Cat A vertical tray fire test
Resistance | Crush & rodent barrier | Steel wire armour ('Z') provides full mechanical & rodent protection
Resistance | ATEX & direct burial | Approved for direct soil burial and ATEX Zone 1/2 pipe racks
Standards | Italian & IEC standards | CEI 20-13 · CEI UNEL 35027 · IEC 60502-2
Standards | Armour wire standard | EN 10257-1 hot-dip galvanized round steel wire
Standards | RoHS, REACH & CE | 2011/65/EU RoHS 2, REACH & CE compliant
Identification | CEI code breakdown | R=Cu · G7=HEPR · H1=Cu screen · O=3-core · Z=Steel wire armour · R=PVC
Identification | Outer sheath colour | Red (RAL 3000)
Identification | Customs tariff (HS) | 8544.6010

## Construction
RG7H1OZR Three-Core Screened Armoured MV Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1ozr-three-core-screened-armoured-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3 × Class 2 compacted circular red copper conductors ('R') | Stranded compacted annealed plain copper per CEI EN 60228 Class 2 (3 × 25 mm² to 3 × 240 mm²)
2 | Triple-extruded inner & cold-strippable outer semicon screens | Thermoset semiconducting conductor screen and easy-peel outer insulation screen on each phase core
3 | +105 °C G7 High-Modulus HEPR dielectric insulation | Hard-grade Ethylene Propylene Rubber compound Type G7 per CEI 20-11 (+105 °C continuous, +250 °C short-circuit)
4 | 3 × Individual H1 copper screens + inner PVC bedding ('O') | Helically applied red copper tape/wire screen on each phase core (total ≥ 16 mm²) + extruded PVC inner bedding over laid-up cores
5 | Galvanized round steel wire armour ('Z' = Filo d'acciaio) | Concentric helical layer of hot-dip galvanized round steel wires (1.6 mm to 2.5 mm diameter)
6 | Overall Red flame-retardant PVC outer sheath ('R', Type Rz) | Lead-free flame-retardant PVC compound Type Rz per CEI 20-11 in Red (RAL 3000)
| RG7H1OZR 8.7/15 kV (3×25 to 3×240 mm²) | 8.7/15 kV (Umax 17.5 kV, 3.6 mm G7 wall) three-core screened & SWA armoured MV cable for 15 kV refineries and rocky burial
| RG7H1OZR 12/20 kV (3×35 to 3×240 mm²) | 12/20 kV (Umax 24 kV, 4.5 mm G7 wall) three-core screened & SWA armoured MV cable for 20 kV industrial & mining networks
| RG7H1OZR 18/30 kV (3×50 to 3×185 mm²) | 18/30 kV (Umax 36 kV, 6.5 mm G7 wall) three-core screened & SWA armoured MV cable for 30/33 kV heavy infrastructure

## Quality and supply
RG7H1OZR Three-Core Screened Armoured MV Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1ozr-three-core-screened-armoured-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 3.5 × Uo AC voltage test (42 kV on 12/20 kV) & PD test (< 5 pC) — Zero breakdown for 5 min and partial discharge ≤ 5 pC at 1.73 × Uo | Every manufactured drum
Type test | CEI 20-22 II Cat A bunched flame, G7 hot-set & 125 kV BIL impulse test — Passes Cat A vertical tray fire and lightning impulse withstand | Type qualification
Sample test | Steel wire armour tensile strength, zinc mass & inner bedding thickness — Meets CEI 20-13 / EN 10257-1 mechanical and corrosion specifications | Per production batch
Standard / approval | CEI 20-13 & IEC 60502-2
Standard / approval | CEI 20-22 II Cat A Flame
Standard / approval | ATEX EN 60079-14 Compatible
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX RG7H1OZR 12/20kV CEI 20-13 CEI 20-22 II
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP