## Request a quote
Request a quotation for RG7H1RX
Application engineer · MV distribution cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/rg7h1rx-12-20kv-triplex-copper-hepr-screened-mv-power-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
RG7H1RX 12/20 kV Triplex Copper HEPR MV Power Cable – Dimensions, tensile ratings & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1rx-12-20kv-triplex-copper-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35756 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Weight ≈ kg/km | Tensile load kN ≈ | Min. bend R mm | Series
| RG7H1RX 3×(1×35/16) mm² 12/20 kV | 3 × (1 × 35/16 mm² Cu) | Class 2 Cu + H1 wire/tape screen | 53 | 2490 | 18 | 795 | RG7H1RX Construction Schedule (−25…+90 °C)
| RG7H1RX 3×(1×50/16) mm² 12/20 kV | 3 × (1 × 50/16 mm² Cu) | Class 2 Cu + H1 wire/tape screen | 56 | 2980 | 25.5 | 840 | RG7H1RX Construction Schedule (−25…+90 °C)
| RG7H1RX 3×(1×70/16) mm² 12/20 kV | 3 × (1 × 70/16 mm² Cu) | Class 2 Cu + H1 wire/tape screen | 60 | 3740 | 35.5 | 900 | RG7H1RX Construction Schedule (−25…+90 °C)
| RG7H1RX 3×(1×95/16) mm² 12/20 kV | 3 × (1 × 95/16 mm² Cu) | Class 2 Cu + H1 wire/tape screen | 64 | 4680 | 48 | 960 | RG7H1RX Construction Schedule (−25…+90 °C)
| RG7H1RX 3×(1×120/16) mm² 12/20 kV | 3 × (1 × 120/16 mm² Cu) | Class 2 Cu + H1 wire/tape screen | 68 | 5620 | 60.5 | 1020 | RG7H1RX Construction Schedule (−25…+90 °C)
Custom core counts, cross-sections, sheath colours and factory-tested cut lengths available per CEI UNEL 35756 / IEC 60502-2.

## Electrical, optical & thermal p
RG7H1RX 12/20 kV Triplex Copper HEPR MV Power Cable – Electrical, optical & thermal parameters (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1rx-12-20kv-triplex-copper-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35756 / IEC 60502-2. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Capacity | Operating temp.
3 × (1 × 35/16 mm² Cu) | 0.524 | 12/20 kV / 178 A | −25…+90 °C
3 × (1 × 50/16 mm² Cu) | 0.387 | 12/20 kV / 212 A | −25…+90 °C
3 × (1 × 70/16 mm² Cu) | 0.268 | 12/20 kV / 262 A | −25…+90 °C
3 × (1 × 95/16 mm² Cu) | 0.193 | 12/20 kV / 316 A | −25…+90 °C
3 × (1 × 120/16 mm² Cu) | 0.153 | 12/20 kV / 362 A | −25…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric and dimensional verification.

## Technical data
RG7H1RX 12/20 kV Triplex Copper HEPR MV Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1rx-12-20kv-triplex-copper-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35756 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 12/20 (24) kV (Triplex MV distribution feeder)
Key data | Operating temp. | −25…+90 °C (Continuous thermal operating range)
Key data | Min. bend radius | 15 × OD (Installed / dynamic routing limit)
Key data | Core / conductor | Class 2 Cu (3×(1×compact stranded copper))
Key data | Outer protection | Triplex Rz PVC (3×individual red Rz PVC sheaths)
Key data | Standard | CEI UNEL 35756 (CEI UNEL 35756 / IEC 60502-2)
Electrical | Rated voltage / transmission duty | 12/20 (24) kV (CEI UNEL 35756 / IEC 60502-2)
Electrical | Core / conductor construction | Phase Conductors (3x1x50 mm²) — Class 2 compact circular stranded plain annealed copper conductors (Code R) in a visible three-phase triplex assembly
Electrical | Primary dielectric / insulation | Conductor Screen — Extruded thermosetting semiconductive elastomer conductor screen ensuring void-free interface with the primary dielectric
Thermal | Continuous operating temperature | −25…+90 °C (rated operating envelope)
Thermal | Storage & transport temperature | −40…+80 °C on export drum or reel
Mechanical | Outer protection / sheath | Triplex Phase Jackets (RX) — Three individual flame-retardant red Rz PVC outer sheaths helically cabled into a self-supporting triplex bundle (RX)
Mechanical | Minimum bending radius | 15 × OD
Mechanical | Structural layer count | 6 concentric functional layers
Resistance | Environmental & chemical resistance | Industrial moisture, oils and mechanical wear per CEI UNEL 35756 / IEC 60502-2
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | CEI UNEL 35756 / IEC 60502-2
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | RG7H1RX
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
RG7H1RX 12/20 kV Triplex Copper HEPR MV Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1rx-12-20kv-triplex-copper-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35756 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase Conductors (3x1x50 mm²) | Class 2 compact circular stranded plain annealed copper conductors (Code R) in a visible three-phase triplex assembly | CEI UNEL 35756 / IEC 60502-2
2 | Conductor Screen | Extruded thermosetting semiconductive elastomer conductor screen ensuring void-free interface with the primary dielectric | CEI UNEL 35756 / IEC 60502-2
3 | MV Primary Insulation (G7) | High-modulus ethylene propylene rubber (G7 HEPR) primary insulation rated for 90 °C continuous / 250 °C short-circuit service | CEI UNEL 35756 / IEC 60502-2
4 | Insulation Screen | Cold-strippable extruded outer semiconductive elastomer insulation screen for clean medium-voltage termination | CEI UNEL 35756 / IEC 60502-2
5 | Metallic Phase Screen (H1) | Concentric layer of plain copper wires bound by an open counter-helix copper equalizing tape (H1) over each phase | CEI UNEL 35756 / IEC 60502-2
6 | Triplex Phase Jackets (RX) | Three individual flame-retardant red Rz PVC outer sheaths helically cabled into a self-supporting triplex bundle (RX) | CEI UNEL 35756 / IEC 60502-2
| RG7H1RX — Standard Execution | Built to CEI UNEL 35756 / IEC 60502-2 with phase conductors (3x1x50 mm²) and triplex phase jackets (rx)
| RG7H1RX — Custom Length & Configuration | Available in custom drum lengths, core counts or factory-terminated assemblies
| RG7H1RX — Factory Routine Certified | Supplied with EN 10204 3.1 routine electrical, dielectric & dimensional inspection report

## Quality and supply
RG7H1RX 12/20 kV Triplex Copper HEPR MV Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1rx-12-20kv-triplex-copper-hepr-screened-mv-power-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on CEI UNEL 35756 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance & dimensional verification (CEI UNEL 35756 / IEC 60502-2) — Electrical parameters and outer diameter within CEI UNEL 35756 / IEC 60502-2 tolerances | Every manufactured drum / length
Routine test | High-voltage dielectric & insulation resistance test (CEI UNEL 35756 / IEC 60502-2) — Zero dielectric breakdown and verified insulation resistance over full length | Every manufactured drum / length
Type test | Thermal ageing, mechanical flexing & environmental qualification (CEI UNEL 35756 / IEC 60502-2) — Verified structural and dielectric integrity across −25…+90 °C | Type qualification & periodic lot audit
Standard / approval | CEI UNEL 35756 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX RG7H1RX CEI UNEL 35756 12/20 (24) kV CE
Supply | Delivery form: Heavy-duty export wooden/steel drums or factory-tested coils
Supply | Standard lengths: 100 m, 250 m, 500 m, 1,000 m or custom cut-to-length reels
Supply | MOQ: 100 m (standard configurations) · 300 m (custom builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP