## Request a quote
Request a quotation for RG7H1R
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/rg7h1r-single-core-hepr-insulated-mv-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
RG7H1R Single-Core HEPR-Insulated MV Cable – 12/20 kV dimensions & CEI UNEL 35027 ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1r-single-core-hepr-insulated-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2 / CEI UNEL 35375. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | CEI designation | Conductor / screen | Outer Ø ≈ mm | Weight ≈ kg/km | Air 30°C A | Buried 20°C A | Series
| RG7H1R 1×35/16 12/20kV | 35 mm² Cl.2 Cu + 16 mm² Cu screen | 23.5 | 790 | 198 | 182 | 12/20 kV RG7H1R Single-Core (16 mm² Cu Screen)
| RG7H1R 1×50/16 12/20kV | 50 mm² Cl.2 Cu + 16 mm² Cu screen | 24.8 | 935 | 238 | 215 | 12/20 kV RG7H1R Single-Core (16 mm² Cu Screen)
| RG7H1R 1×95/16 12/20kV | 95 mm² Cl.2 Cu + 16 mm² Cu screen | 28.2 | 1410 | 362 | 315 | 12/20 kV RG7H1R Single-Core (16 mm² Cu Screen)
| RG7H1R 1×150/16 12/20kV | 150 mm² Cl.2 Cu + 16 mm² Cu screen | 31.2 | 1960 | 472 | 398 | 12/20 kV RG7H1R Single-Core (16 mm² Cu Screen)
| RG7H1R 1×240/16 12/20kV | 240 mm² Cl.2 Cu + 16 mm² Cu screen | 35.6 | 2890 | 635 | 518 | 12/20 kV RG7H1R Single-Core (16 mm² Cu Screen)
| RG7H1R 1×400/16 12/20kV | 400 mm² Cl.2 Cu + 16 mm² Cu screen | 41.2 | 4380 | 845 | 660 | 12/20 kV RG7H1R Single-Core (16 mm² Cu Screen)
Ampacity in trefoil formation at +105 °C conductor temperature per CEI UNEL 35027. Also available in 8.7/15 kV and 18/30 kV.

## Technical data
RG7H1R Single-Core HEPR-Insulated MV Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1r-single-core-hepr-insulated-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2 / CEI UNEL 35375. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | CEI 20-13 / UNEL (& IEC 60502-2 MV Power)
Key data | Voltage classes | 8.7/15 to 18/30 (Also 3.6/6 kV & 6/10 kV)
Key data | Cross-sections | 1 × 25 to 630 mm (Class 2 compacted red Cu ('R'))
Key data | Insulation | G7 HEPR (+105 °C (High-modulus EPR (+250 °C SC))
Key data | Metallic screen | H1 (≥ 16 mm² Cu) (Copper tape or concentric wire)
Key data | Outer sheath | Red PVC Type Rz (CEI 20-22 II / IEC 60332-3)
Electrical | Rated voltage tiers (Uo/U) | 6/10 kV · 8.7/15 kV · 12/20 kV · 18/30 kV (Umax 12 / 17.5 / 24 / 36 kV)
Electrical | Routine AC test voltage | 21 kV (6/10) · 30.5 kV (8.7/15) · 42 kV (12/20) · 63 kV (18/30) (3.5 × Uo)
Electrical | Partial discharge limit | ≤ 5 pC at 1.73 × Uo ambient and after heating cycle
Electrical | Max. DC resistance @ 20 °C | 0.387 Ω/km (50) · 0.193 Ω/km (95) · 0.124 Ω/km (150) · 0.0754 Ω/km (240)
Thermal | Continuous conductor temp. | +105 °C (G7 HEPR rating per CEI 20-13)
Thermal | Emergency overload temp. | +140 °C
Thermal | Short-circuit temperature | +250 °C (max. 5 s)
Mechanical | G7 HEPR wall thickness | 3.6 mm (8.7/15 kV) · 4.5 mm (12/20 kV) · 6.5 mm (18/30 kV) reduced wall
Mechanical | Min. bend radius | 14 × OD (during pulling) · 12 × OD (final fixed position)
Mechanical | Max. pulling tension | 50 N / mm² of copper conductor section with pulling stocking/eye
Resistance | Bunched flame propagation | CEI 20-22 II & IEC 60332-3-22 Cat A vertical tray fire test
Resistance | Hydrogen chloride emission | CEI 20-37 / EN 60754-1: ≤ 18 % HCl (reduced-halogen Rz PVC)
Resistance | Moisture & direct burial | Suitable for indoor trays, outdoor racks, underground ducts & direct burial
Standards | Italian & IEC standards | CEI 20-13 · CEI UNEL 35375 / 35376 · IEC 60502-2
Standards | Ampacity tables | CEI UNEL 35027 (+105 °C MV current rating tables)
Standards | RoHS, REACH & CE | 2011/65/EU RoHS 2, REACH & CE compliant
Identification | CEI code breakdown | R=Cu Cl.2 · G7=HEPR 105°C · H1=Cu tape/wire screen · R=Red PVC Rz sheath
Identification | Outer sheath colour | Red (RAL 3000) for MV identification
Identification | Customs tariff (HS) | 8544.6010

## Construction
RG7H1R Single-Core HEPR-Insulated MV Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1r-single-core-hepr-insulated-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2 / CEI UNEL 35375. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 2 compacted circular red copper conductor ('R') | Stranded compacted annealed plain copper ('R' = Rame cordato rotondo compatto) per CEI EN 60228 Class 2 (25 to 630 mm²)
2 | Triple-extruded inner & outer semiconducting stress screens | Cross-linked semiconducting elastomer bonded to conductor and cold-strippable outer semiconducting layer over G7 dielectric
3 | +105 °C G7 High-Modulus HEPR dielectric insulation | Hard-grade Ethylene Propylene Rubber compound Type G7 per CEI 20-11 (+105 °C continuous, +140 °C overload, +250 °C short-circuit)
4 | H1 Metallic copper earth screen (≥ 16 mm²) | Helically applied overlapped annealed red copper tape (0.15 mm) or concentric copper wires ('H16' = 16 mm² nominal geometric section)
5 | Red flame-retardant PVC outer sheath ('R', Type Rz) | Lead-free flame-retardant polyvinyl chloride compound Type Rz per CEI 20-11 in Red (RAL 3000)
| RG7H1R 8.7/15 kV (1×25/16 to 1×630/16 mm²) | 8.7/15 kV (Umax 17.5 kV, 3.6 mm G7 wall) single-core MV cable for 15 kV Italian & international utility networks
| RG7H1R 12/20 kV (1×35/16 to 1×630/16 mm²) | 12/20 kV (Umax 24 kV, 4.5 mm G7 wall) single-core MV cable for 20 kV industrial distribution and renewable substations
| RG7H1R 18/30 kV (1×50/16 to 1×630/16 mm²) | 18/30 kV (Umax 36 kV, 6.5 mm G7 wall) single-core MV cable for 30/33 kV primary grid and wind/solar collector feeders

## Quality and supply
RG7H1R Single-Core HEPR-Insulated MV Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7h1r-single-core-hepr-insulated-mv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / IEC 60502-2 / CEI UNEL 35375. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 3.5 × Uo AC voltage test (42 kV on 12/20 kV) & PD test (< 5 pC) — Zero breakdown for 5 min and partial discharge ≤ 5 pC at 1.73 × Uo | Every manufactured drum
Type test | G7 HEPR elastic modulus (≥ 4.5 MPa at +150 °C) & 175 kV impulse BIL test — Passes 10 positive + 10 negative lightning impulses at +110 °C | Type qualification
Sample test | CEI 20-22 II Cat A vertical tray fire & outer semicon peel force test — Char height ≤ 2.5 m and clean cold-strippable semicon removal | Per production batch
Standard / approval | CEI 20-13 & CEI UNEL 35375
Standard / approval | IEC 60502-2 Compliant
Standard / approval | CEI 20-22 II Flame Cat A
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX RG7H1R 12/20kV CEI 20-13 CEI 20-22 II
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP