## Request a quote
Request a quotation for RG7OZR
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/rg7ozr-three-core-armoured-hepr-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
RG7OZR Three-Core Armoured HEPR Power Cable – 0.6/1 kV 3-core SWA dimensions & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7ozr-three-core-armoured-hepr-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / CEI 20-14 / IEC 60502-1 / CEI UNEL 35377. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | CEI designation | Conductors & SWA wire | Outer Ø ≈ mm | Weight ≈ kg/km | Air 30°C A | Buried 20°C A | Series
| RG7OZR 3×6 mm² 0.6/1kV | 3 × 6 mm² Cu + 0.9 mm SWA | 16.8 | 540 | 54 | 62 | 0.6/1 kV RG7OZR Three-Core Steel-Wire-Armoured Cables
| RG7OZR 3×16 mm² 0.6/1kV | 3 × 16 mm² Cu + 1.25 mm SWA | 21.8 | 1060 | 100 | 107 | 0.6/1 kV RG7OZR Three-Core Steel-Wire-Armoured Cables
| RG7OZR 3×35 mm² 0.6/1kV | 3 × 35 mm² Cu + 1.6 mm SWA | 27.6 | 1980 | 162 | 162 | 0.6/1 kV RG7OZR Three-Core Steel-Wire-Armoured Cables
| RG7OZR 3×70 mm² 0.6/1kV | 3 × 70 mm² Cu + 1.6 mm SWA | 34.8 | 3380 | 250 | 236 | 0.6/1 kV RG7OZR Three-Core Steel-Wire-Armoured Cables
| RG7OZR 3×120 mm² 0.6/1kV | 3 × 120 mm² Cu + 2.0 mm SWA | 43.2 | 5490 | 352 | 318 | 0.6/1 kV RG7OZR Three-Core Steel-Wire-Armoured Cables
| RG7OZR 3×185 mm² 0.6/1kV | 3 × 185 mm² Cu + 2.5 mm SWA | 52 | 8240 | 456 | 398 | 0.6/1 kV RG7OZR Three-Core Steel-Wire-Armoured Cables
Also available in 3G (with GNYE), 4×, 4G, 5G and 1.8/3 kV configurations.

## Technical data
RG7OZR Three-Core Armoured HEPR Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7ozr-three-core-armoured-hepr-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / CEI 20-14 / IEC 60502-1 / CEI UNEL 35377. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | CEI 20-13 / CEI (CEI UNEL 35377 & IEC 60502-1)
Key data | Voltage classes | 0.6/1 kV & 1.8/3 (Low- & lower-medium voltage)
Key data | Cross-sections | 3×1.5 to 3×240 m (Also 4G, 5G & multi-core)
Key data | Insulation | G7 HEPR (+90/+10 (High-modulus EPR (+250 °C SC))
Key data | Armour ('Z') | Galv. Steel Wire (Round SWA tensile & crush shield)
Key data | Outer sheath | Grey/Red PVC Typ (CEI 20-22 II Cat A flame)
Electrical | Rated voltage (Uo/U) | 0.6 / 1 kV AC (CEI UNEL 35377) · 1.8 / 3 kV AC (CEI 20-13)
Electrical | Routine AC test voltage | 4,000 V AC (0.6/1 kV) · 6,500 V AC (1.8/3 kV) for 5 minutes
Electrical | Max. DC resistance @ 20 °C | 1.91 Ω/km (10) · 1.21 Ω/km (16) · 0.387 Ω/km (50) · 0.193 Ω/km (95)
Electrical | Insulation resistance | Kᵢ ≥ 5,000 MΩ·km at 20 °C
Thermal | Continuous conductor temp. | +90 °C (0.6/1 kV UNEL 35377) / +105 °C (G7 compound rating)
Thermal | Short-circuit temperature | +250 °C (max. 5 s)
Thermal | Ambient temperature range | -15 °C to +80 °C (fixed) · 0 °C to +50 °C (during laying)
Mechanical | Steel wire armour ('Z') | Galvanized round steel wires (≥ 90 % coverage) with 350–500 N/mm² tensile
Mechanical | Min. bend radius | 12 × overall cable OD
Mechanical | Impact & crush resistance | Passes IEC 60502-1 heavy mechanical impact and direct-burial crush
Resistance | Bunched flame propagation | CEI 20-22 II & IEC 60332-3-22 Cat A vertical tray fire test
Resistance | Reduced halogen emission | CEI 20-37 / EN 60754-1: ≤ 18 % HCl
Resistance | Rodent & termite barrier | Concentric steel wire armour provides 100 % rodent immunity
Standards | Italian & IEC standards | CEI 20-13 · CEI 20-14 · CEI UNEL 35377 · IEC 60502-1
Standards | ATEX plant installation | Suitable for Zone 1 / Zone 2 hazardous areas per EN 60079-14 with Ex glands
Standards | RoHS, REACH & CE | 2011/65/EU RoHS 2, REACH & CE compliant
Identification | CEI code breakdown | R=Cu · G7=HEPR · O=Multi-core+bedding · Z=Steel wire armour · R=PVC Rz
Identification | Core colours (HD 308 S2) | 3C: Brown, Black, Grey (or GNYE, Blue, Brown) · 4C/5C: HD 308 S2
Identification | Customs tariff (HS) | 8544.4993 (0.6/1 kV) · 8544.6010 (1.8/3 kV)

## Construction
RG7OZR Three-Core Armoured HEPR Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7ozr-three-core-armoured-hepr-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / CEI 20-14 / IEC 60502-1 / CEI UNEL 35377. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3 (or 3G / 4G / 5G) × Annealed red copper conductors ('R') | Class 5 flexible or Class 2 stranded annealed plain copper per CEI EN 60228 (1.5 mm² to 240 mm²)
2 | G7 High-Modulus HEPR elastomer core insulation | Cross-linked high-modulus ethylene propylene rubber compound Type G7 per CEI 20-11, colour-coded per HD 308 S2 / CEI UNEL 00722
3 | Extruded flame-retardant inner bedding sheath ('O') | Extruded thermoplastic inner sheath filling core interstices into a smooth cylindrical bedding
4 | Galvanized round steel wire armour ('Z' = Filo d'acciaio) | Concentric layer of hot-dip galvanized round steel wires (0.9 mm to 2.5 mm diameter depending on cable OD)
5 | Flame-retardant PVC outer sheath ('R', Type Rz) | Lead-free flame-retardant PVC Type Rz in Grey (RAL 7001 for 0.6/1 kV) or Red (for 1.8/3 kV)
| RG7OZR 0.6/1 kV (3×1.5 to 3×240 / 4G / 5G mm² · Grey) | CEI UNEL 35377 0.6/1 kV steel-wire-armoured G7 HEPR power cable with Grey Rz outer sheath (replacing FG7OZR where Class 2/5 R specified)
| RG7OZR 1.8/3 kV (3×16 to 3×240 mm² · Red) | CEI 20-13 1.8/3 kV unscreened steel-wire-armoured G7 HEPR power cable for 3 kV industrial motors and auxiliary feeders

## Quality and supply
RG7OZR Three-Core Armoured HEPR Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/rg7ozr-three-core-armoured-hepr-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI 20-13 / CEI 20-14 / IEC 60502-1 / CEI UNEL 35377. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 4.0 kV (0.6/1 kV) or 6.5 kV (1.8/3 kV) AC dielectric & DC R test — Zero breakdown for 5 min and DC resistance within CEI EN 60228 limits | Every manufactured drum
Type test | CEI 20-22 II Cat A bunched vertical flame & G7 HEPR hot-set test — Char height ≤ 2.5 m and G7 elastic modulus ≥ 4.5 MPa at +150 °C | Type qualification
Sample test | Galvanized steel wire armour tensile strength & zinc coating test — Meets EN 10257-1 / CEI 20-14 zinc mass and wire diameter tolerances | Per production batch
Standard / approval | CEI 20-13 & CEI 20-14
Standard / approval | CEI UNEL 35377 & IEC 60502-1
Standard / approval | CEI 20-22 II Cat A Flame
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX RG7OZR 0.6/1kV CEI UNEL 35377 CEI 20-22 II
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP