## Request a quote
Request a quotation for RTD Extension Cable
Application engineer · temperature & process instrumentation
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/rtd-extension-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
RTD Extension Cable – Dimensions, construction & weights (17)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rtd-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60751 / BS EN 50288-7 / ASTM E1137. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Insulation / Screen / Sheath | Temp. range | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| RTD-PVC-OS 1×3×0.5 | 1 Triad (3-wire) × 0.5 mm² | PVC / PVC (OS) | −30…+105 °C | 5.9 | 17 | 50 | 44 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-PVC-OS 1×4×0.5 | 1 Quad (4-wire) × 0.5 mm² | PVC / PVC (OS) | −30…+105 °C | 6.4 | 22 | 58 | 48 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-PVC-OS 1×3×0.75 | 1 Triad (3-wire) × 0.75 mm² | PVC / PVC (OS) | −30…+105 °C | 6.4 | 24 | 62 | 48 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-PVC-OS 1×4×0.75 | 1 Quad (4-wire) × 0.75 mm² | PVC / PVC (OS) | −30…+105 °C | 7 | 31 | 74 | 52 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-PVC-TiMF 4×3×0.75 | 4 Triads (3-wire) × 0.75 mm² | PVC / PVC (TiMF+OS) | −30…+105 °C | 13.4 | 98 | 224 | 100 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-PVC-TiMF 8×3×0.75 | 8 Triads (3-wire) × 0.75 mm² | PVC / PVC (TiMF+OS) | −30…+105 °C | 17.8 | 192 | 396 | 134 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-PVC-TiMF 12×3×0.75 | 12 Triads (3-wire) × 0.75 mm² | PVC / PVC (TiMF+OS) | −30…+105 °C | 21.4 | 286 | 568 | 160 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-PVC-OS 1×3×1.0 | 1 Triad (3-wire) × 1.0 mm² | PVC / PVC (OS) | −30…+105 °C | 6.8 | 31 | 74 | 51 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-PVC-TiMF 4×3×1.0 | 4 Triads (3-wire) × 1.0 mm² | PVC / PVC (TiMF+OS) | −30…+105 °C | 14.2 | 128 | 268 | 106 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-PVC-OS 1×3×1.5 | 1 Triad (3-wire) × 1.5 mm² | PVC / PVC (OS) | −30…+105 °C | 7.6 | 46 | 98 | 57 | Tinned Copper / PVC Screened 3-Wire & 4-Wire Process Cables (−30…+105 °C)
| RTD-SPC-FEP 1×3×0.22 | 1 Triad (3-wire) × 0.22 mm² SPC | FEP / SPC Braid / FEP | −190…+200 °C | 3.4 | 11 | 24 | 26 | Silver/Nickel-Plated Copper / FEP & PTFE Probe & Autoclave Leads (−190…+260 °C)
| RTD-SPC-FEP 1×4×0.22 | 1 Quad (4-wire) × 0.22 mm² SPC | FEP / SPC Braid / FEP | −190…+200 °C | 3.7 | 14 | 29 | 28 | Silver/Nickel-Plated Copper / FEP & PTFE Probe & Autoclave Leads (−190…+260 °C)
| RTD-SPC-FEP 1×3×0.5 | 1 Triad (3-wire) × 0.5 mm² SPC | FEP / SPC Braid / FEP | −190…+200 °C | 4.5 | 20 | 44 | 34 | Silver/Nickel-Plated Copper / FEP & PTFE Probe & Autoclave Leads (−190…+260 °C)
| RTD-SPC-FEP 1×4×0.5 | 1 Quad (4-wire) × 0.5 mm² SPC | FEP / SPC Braid / FEP | −190…+200 °C | 4.9 | 25 | 52 | 37 | Silver/Nickel-Plated Copper / FEP & PTFE Probe & Autoclave Leads (−190…+260 °C)
| RTD-NPC-PTFE 1×3×0.5 | 1 Triad (3-wire) × 0.5 mm² NPC | PTFE / NPC Braid / PTFE | −190…+260 °C | 4.6 | 20 | 46 | 34 | Silver/Nickel-Plated Copper / FEP & PTFE Probe & Autoclave Leads (−190…+260 °C)
| RTD-XLPE-SWA 1×3×1.5 | 1 Triad (3-wire) × 1.5 mm² | XLPE / SWA / LSZH | −40…+90 °C | 12.2 | 46 | 305 | 122 | XLPE / LSZH / SWA Armoured Multi-Triad Refinery Trunks (−40…+90 °C)
| RTD-XLPE-SWA 4×3×1.5 | 4 Triads (3-wire) × 1.5 mm² | XLPE / SWA / LSZH | −40…+90 °C | 20.6 | 182 | 815 | 206 | XLPE / LSZH / SWA Armoured Multi-Triad Refinery Trunks (−40…+90 °C)
Specify IEC 60751 (Red/White/White) or EN 50288-7 (Black/White/Red) core colours when ordering.

## Leadwire resistance & Pt100 err
RTD Extension Cable – Leadwire resistance & Pt100 error analysis by cross-section (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/rtd-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60751 / BS EN 50288-7 / ASTM E1137. Values for your order are confirmed in the quotation.
Conductor size | Max. R₂₀ / core Ω/km | 2-Wire Pt100 error per 10 m run | 3-Wire Pt100 error per 100 m (matched) | 4-Wire Kelvin error per 100 m
0.22 mm² (AWG 24) | 84.8 | +4.41 °C | ≤ 0.08 °C | 0.00 °C (negligible)
0.50 mm² (AWG 20) | 36.7 | +1.91 °C | ≤ 0.05 °C | 0.00 °C (negligible)
0.75 mm² (AWG 18) | 25 | +1.30 °C | ≤ 0.04 °C | 0.00 °C (negligible)
1.00 mm² (AWG 17) | 18.5 | +0.96 °C | ≤ 0.03 °C | 0.00 °C (negligible)
1.50 mm² (AWG 16) | 12.3 | +0.64 °C | ≤ 0.02 °C | 0.00 °C (negligible)
A 2-wire Pt100 adds 2 × R_lead directly to the 100 Ω element (+0.385 Ω/°C). A 3-wire bridge cancels R_lead provided all 3 cores have identical resistance.

## Technical data
RTD Extension Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/rtd-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60751 / BS EN 50288-7 / ASTM E1137. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Sensor types | Pt100 / Pt1000 (also Pt500, Ni100, Cu50 RTDs)
Key data | Configurations | 3-Wire / 4-Wire (1×3 to 24×3 triads · 1×4 quads)
Key data | Core R balance | ΔR ≤ 0.01 Ω/m (matched within each triad/quad)
Key data | IEC colour code | Rd/Wh/Wh (3-W) (Rd/Rd/Wh/Wh (4-W) per IEC 60751)
Key data | Conductors | Cu / TC / SPC (Tinned, Silver- or Nickel-plated)
Key data | Temp. range | −190…+260 °C (FEP/PTFE · −40…+105 °C PVC/LSZH)
Electrical | Supported RTD standards | IEC 60751 / ASTM E1137 (Pt100, Pt500, Pt1000, α = 0.00385 °C⁻¹)
Electrical | Core-to-core DC resistance balance | ΔR ≤ 0.01 Ω/m within any triad/quad (≤ 1 % of conductor R₂₀)
Electrical | Max. conductor DC resistance @ 20 °C | 36.7 (0.5) · 25.0 (0.75) · 18.5 (1.0) · 12.3 Ω/km (1.5 mm²)
Electrical | Insulation resistance @ 20 °C | ≥ 100 MΩ·km (PVC) · ≥ 5000 MΩ·km (XLPE / FEP / PTFE)
Electrical | Operating voltage rating | 300/500 V (process PVC/XLPE) · 300 V (FEP/PTFE sensor leads)
Thermal | Operating temperature (PVC / XLPE-LSZH) | −30 °C to +105 °C (HR-PVC) · −40 °C to +90 °C (XLPE/LSZH)
Thermal | Operating temp. (SPC-FEP / NPC-PTFE) | −190 °C to +200 °C (SPC/FEP) · −190 °C to +260 °C (NPC/PTFE)
Mechanical | Conductor stranding | Class 5 flexible (19-wire SPC/NPC or 24/32-wire TC) or Class 2 (7-wire)
Mechanical | Min. bending radius | 7.5 × OD (unarmoured) · 10 × OD (SWA armoured)
Resistance | Flame retardance | IEC 60332-1-2 & IEC 60332-3-24 Cat C (UL 94 V-0 on FEP/PTFE)
Resistance | Chemical & steam resistance | FEP/PTFE grades impervious to CIP/SIP steam, oils and solvents
Standards | RTD & cable standards | IEC 60751, ASTM E1137 & BS EN 50288-7
Standards | Hazardous area compatibility | Suitable for Ex-i intrinsic safety loops (IEC 60079-14) with Blue sheath
Identification | IEC 60751 core colours | 3-wire: Red / White / White · 4-wire: Red / Red / White / White
Identification | EN 50288-7 multi-triad colours | Black / White / Red numbered 1, 2, 3…
Identification | Customs tariff (HS) | 8544.49

## Construction
RTD Extension Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/rtd-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60751 / BS EN 50288-7 / ASTM E1137. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Resistance-matched copper conductors | Tinned copper (TC up to +105 °C), Silver-plated copper (SPC up to +200 °C) or Nickel-plated copper (NPC up to +260 °C), drawn from a single wire lot
2 | Precision concentric core insulation | PVC, XLPE, FEP (−190…+200 °C) or PTFE (−190…+260 °C) in IEC 60751 Red/White/White (3-wire) or Red/Red/White/White (4-wire)
3 | Al/PET foil and/or SPC wire braid screen | 100 % Al/PET tape + drain wire (OS / TiMF+OS) or ≥ 85 % silver-plated copper braid on FEP/PTFE sensor leads
4 | Optional SWA armour | Unarmoured or Galvanised Steel Wire Armour (SWA) on multi-triad process trunks
5 | Outer jacket (Grey, Black, White or Ex-i Blue) | Flame-retardant PVC, Low-Smoke Zero-Halogen (LSZH), FEP or PTFE | IEC 60332-1-2 / IEC 60332-3-24 flame retardant
| 3-Wire Triad — IEC 60751 (Rd/Wh/Wh) | 1 Red + 2 White cores (or EN 50288-7 Black/White/Red numbered triads) for industrial 3-wire Pt100 bridges
| 4-Wire Quad — IEC 60751 (Rd/Rd/Wh/Wh) | 2 Red + 2 White cores in star-quad lay for Class AA / custody-transfer 4-wire Kelvin Pt100 loops
| SPC / FEP Sensor Lead (−190…+200 °C) | Silver-plated copper + FEP insulation + SPC braid + FEP jacket for direct RTD probe termination

## Quality and supply
RTD Extension Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/rtd-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60751 / BS EN 50288-7 / ASTM E1137. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Core-to-core DC resistance balance & continuity test — R₂₀ per IEC 60228 and ΔR ≤ 0.01 Ω/m between cores of each triad/quad | Every manufactured drum
Routine test | 1500 V / 2000 V AC dielectric withstand test — 1 min AC test without breakdown; IR ≥ 100 MΩ·km (PVC) or ≥ 5000 MΩ·km (XLPE/FEP) | Every manufactured drum
Standard / approval | IEC 60751 & ASTM E1137 RTD Compatible
Standard / approval | BS EN 50288-7 & IEC 60332-3-24 Cat C
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX RTD EXTENSION CABLE <size> IEC 60751 EN 50288-7 CE
Supply | Delivery form: Non-returnable fumigated wooden drums
Supply | Standard lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP