## Request a quote
Request a quotation for S05BC4B-F / S07BC4B-F / S1BC4B-F
Specify voltage series — S05BC4B-F (300/500 V), S07BC4B-F (450/750 V), or S1BC4B-F (0.6/1 kV) — core count, cross-section, and drum length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/s05bc4b-f-s07bc4b-f-s1bc4b-f-screened-epr-flexible-industrial-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
S05BC4B-F / S07BC4B-F / S1BC4B-F Screened EPR Flexible Industrial – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s05bc4b-f-s07bc4b-f-s1bc4b-f-screened-epr-flexible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Type, Voltage & Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| S05BC4B-F 4G1.0 (300/500 V) | 300/500 V 4G1.0 | 1.0 | 10.2 | 64 | 152 | 51 | S05BC4B-F (300/500 V) — Screened EPR control & instrumentation
| S05BC4B-F 7G1.5 (300/500 V) | 300/500 V 7G1.5 | 1.5 | 14.2 | 145 | 295 | 71 | S05BC4B-F (300/500 V) — Screened EPR control & instrumentation
| S05BC4B-F 12G1.5 (300/500 V) | 300/500 V 12G1.5 | 1.5 | 18 | 235 | 465 | 90 | S05BC4B-F (300/500 V) — Screened EPR control & instrumentation
| S05BC4B-F 18G1.5 (300/500 V) | 300/500 V 18G1.5 | 1.5 | 20.8 | 340 | 640 | 104 | S05BC4B-F (300/500 V) — Screened EPR control & instrumentation
| S07BC4B-F 4G1.5 (450/750 V) | 450/750 V 4G1.5 | 1.5 | 11.8 | 92 | 205 | 59 | S07BC4B-F (450/750 V) & S1BC4B-F (0.6/1 kV) — Screened EPR power & VFD
| S07BC4B-F 4G2.5 (450/750 V) | 450/750 V 4G2.5 | 2.5 | 13.8 | 142 | 285 | 69 | S07BC4B-F (450/750 V) & S1BC4B-F (0.6/1 kV) — Screened EPR power & VFD
| S07BC4B-F 4G4.0 (450/750 V) | 450/750 V 4G4.0 | 4.0 | 16 | 212 | 395 | 80 | S07BC4B-F (450/750 V) & S1BC4B-F (0.6/1 kV) — Screened EPR power & VFD
| S07BC4B-F 4G6.0 (450/750 V) | 450/750 V 4G6.0 | 6.0 | 18 | 302 | 525 | 90 | S07BC4B-F (450/750 V) & S1BC4B-F (0.6/1 kV) — Screened EPR power & VFD
| S1BC4B-F 4G10 (0.6/1 kV) | 0.6/1 kV 4G10 | 10 | 22.8 | 485 | 845 | 114 | S07BC4B-F (450/750 V) & S1BC4B-F (0.6/1 kV) — Screened EPR power & VFD
| S1BC4B-F 4G16 (0.6/1 kV) | 0.6/1 kV 4G16 | 16 | 26.2 | 735 | 1185 | 131 | S07BC4B-F (450/750 V) & S1BC4B-F (0.6/1 kV) — Screened EPR power & VFD
| S1BC4B-F 4G25 (0.6/1 kV) | 0.6/1 kV 4G25 | 25 | 31 | 1110 | 1720 | 155 | S07BC4B-F (450/750 V) & S1BC4B-F (0.6/1 kV) — Screened EPR power & VFD
| S1BC4B-F 4G35 (0.6/1 kV) | 0.6/1 kV 4G35 | 35 | 34.6 | 1520 | 2240 | 173 | S07BC4B-F (450/750 V) & S1BC4B-F (0.6/1 kV) — Screened EPR power & VFD
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per EN 50525-2-21 / HD 361 / VDE 0285.

## Electrical & ampacity data
S05BC4B-F / S07BC4B-F / S1BC4B-F Screened EPR Flexible Industrial – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s05bc4b-f-s07bc4b-f-s1bc4b-f-screened-epr-flexible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
300/500 V 4G1.0 | 19.5 | 17 | 14 | 79 | 2500
300/500 V 7G1.5 | 13.3 | 22 | 19 | 80 | 2500
300/500 V 12G1.5 | 13.3 | 22 | 19 | 80 | 2500
300/500 V 18G1.5 | 13.3 | 22 | 19 | 80 | 2500
450/750 V 4G1.5 | 13.3 | 22 | 19 | 80 | 2500
450/750 V 4G2.5 | 7.98 | 30 | 26 | 82 | 2500
450/750 V 4G4.0 | 4.95 | 40 | 34 | 84 | 2500
450/750 V 4G6.0 | 3.3 | 51 | 43 | 87 | 2500
0.6/1 kV 4G10 | 1.91 | 70 | 60 | 92 | 2500
0.6/1 kV 4G16 | 1.21 | 93 | 79 | 101 | 2500
0.6/1 kV 4G25 | 0.78 | 123 | 105 | 114 | 2500
0.6/1 kV 4G35 | 0.554 | 152 | 129 | 129 | 2500
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
S05BC4B-F / S07BC4B-F / S1BC4B-F Screened EPR Flexible Industrial – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/s05bc4b-f-s07bc4b-f-s1bc4b-f-screened-epr-flexible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage classes | 05 / 07 / 1 kV (300/500 V · 450/750 V · 0.6/1 kV)
Key data | EMC screening | Tinned Cu 'C4' (≥ 85 % optical braid coverage)
Key data | Conductor max. | +90 °C ('B') (Heat-resistant EPR · +250 °C SC)
Key data | Cold flexibility | -40 °C mobile (-50 °C fixed · Arctic EPR/EPDM)
Key data | Min. bend R | 5 × D / 8 × D (Fixed installation / flexing duty)
Key data | Halogen status | Halogen-free B/B (EPR insulation & EPR outer sheath)
Electrical | Rated voltage (S05 / S07 / S1) | 300/500 V · 450/750 V · 0.6/1 kV
Electrical | Routine AC test voltage | 2.0 kV (S05) / 2.5 kV (S07) / 3.5 kV (S1)
Electrical | Screen optical coverage ('C4') | ≥ 85 % tinned copper wire braid
Electrical | Transfer impedance at 30 MHz | ≤ 250 mΩ/m
Electrical | Conductor stranding class | EN 60228 Class 5
Electrical | Operating frequency | 50 / 60 Hz & VFD PWM
Thermal | Max. conductor operating temp. | +90 °C continuous ('B' EPR)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Mobile flexing ambient range | -40 °C to +60 °C
Thermal | Fixed installation ambient | -50 °C to +80 °C
Thermal | Current rating advantage | +15 % higher ampacity vs +60 °C H07RN-F
Thermal | Min. installation temperature | -40 °C
Mechanical | Min. bend radius (fixed) | 5 × overall diameter (D)
Mechanical | Min. bend radius (flexing) | 8 × overall diameter (D)
Mechanical | Max. tensile pull on copper | 15 N/mm²
Mechanical | Impact & abrasion resistance | Heavy-duty industrial Type EM7 EPR
Mechanical | Sub-zero cold impact | No cracking down to -40 °C
Mechanical | Braid fatigue durability | Fine-wire high-angle tinned Cu braid
Resistance | Halogen-free composition | EN 60754-1/2 halogen-free EPR/EPR
Resistance | Ozone & UV weather resistance | EN 60811-403 ozone-proof EPR sheath
Resistance | Cold-climate flexibility | Remains flexible down to -40 °C
Resistance | Water & humidity resistance | Suitable for damp & outdoor locations
Resistance | EMC electromagnetic shielding | EN 55011 / EN 61800-3 VFD compliant
Resistance | RoHS / REACH status | CE & RoHS 3 compliant
Standards | Designation code system | CENELEC HD 361 S3 ('S..BC4B-F')
Standards | Construction reference standard | EN 50525-2-21 / DIN VDE 0285
Standards | Insulation & sheath standard | EN 50363-1 (EI7) & EN 50363-2-1 (EM7)
Standards | Conductor standard | EN 60228 Class 5
Standards | Halogen test standard | EN 60754-1 / IEC 60754-2
Standards | Quality certification | EN 10204 3.1 mill certificate
Identification | Core identification (≤ 5 cores) | HD 308 S2 colours (with G/Y)
Identification | Core identification (≥ 6 cores) | White numbers on black cores + G/Y
Identification | Outer sheath colour | Black
Identification | Surface marking | TEBAOFLEX S07BC4B-F / S1BC4B-F [n×mm²] CE
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Lot number & year code

## Construction
S05BC4B-F / S07BC4B-F / S1BC4B-F Screened EPR Flexible Industrial – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/s05bc4b-f-s07bc4b-f-s1bc4b-f-screened-epr-flexible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor ('-F') | Class 5 fine-stranded plain or tinned annealed copper wire | EN 60228 Class 5
2 | +90 °C EPR core insulation ('B') | Cross-linked ethylene-propylene elastomer Type EI7 / 3GI3 rated for +90 °C continuous | EN 50363-1
3 | Inner elastomeric bedding | Extruded rubber inner sheath or non-hygroscopic tape wrap over laid-up cores | EN 50525-2-21
4 | Tinned copper braid screen ('C4') | Braided tin-coated copper wires with ≥ 85 % optical coverage for low transfer impedance | HD 361 S3
5 | Cross-linked EPR outer sheath ('B') | Halogen-free, ozone-, UV-, and cold-resistant (-40 °C) ethylene-propylene elastomer | EN 50363-2-1
| S05BC4B-F (300/500 V) | Screened multi-core EPR control, sensor, and instrumentation cable (0.75–2.5 mm², 2 to 24 cores).
| S07BC4B-F (450/750 V) & S1BC4B-F (0.6/1 kV) | Screened heavy-duty EPR power and VFD motor supply cable (1.5–95 mm²).

## Quality and supply
S05BC4B-F / S07BC4B-F / S1BC4B-F Screened EPR Flexible Industrial – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/s05bc4b-f-s07bc4b-f-s1bc4b-f-screened-epr-flexible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage test — 2.0 kV (S05), 2.5 kV (S07), or 3.5 kV (S1) rms for 5 minutes | Every drum
Routine test | Conductor & C4 braid DC resistance — EN 60228 Class 5 conductor & ≥ 85 % braid coverage verified | Every drum
Sample test | -40 °C cold-bend & +90 °C thermal ageing — Passes EN 50363 EI7/EM7 thermal stability and sub-zero bend test | Per batch
Type test | Halogen-free & ozone resistance test — Passes EN 60754-1/2 halogen-free test and EN 60811-403 ozone test | Type approval
Standard / approval | HD 361 / EN 50525-2-21
Standard / approval | EN 60754-1/2
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX S07BC4B-F / S1BC4B-F [n×mm²] +90C
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP