## Request a quote
Request a quotation for S07BB-F / S1BB-F
Specify S07BB-F (450/750 V) or S1BB-F (0.6/1 kV), core count, conductor cross-section (1.5 to 185 mm²), and drum length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/s07bb-f-s1bb-f-heavy-duty-epr-insulated-industrial-flexible-rubber-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
S07BB-F / S1BB-F Heavy-Duty EPR-Insulated Industrial Flexible – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07bb-f-s1bb-f-heavy-duty-epr-insulated-industrial-flexible-rubber-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Type, Voltage & Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| S07BB-F 3G1.5 (450/750 V) | 450/750 V 3G1.5 | 1.5 | 9.8 | 43 | 122 | 39 | S07BB-F (450/750 V) — Heavy-duty +90 °C EPR/EPR flexible rubber
| S07BB-F 3G2.5 (450/750 V) | 450/750 V 3G2.5 | 2.5 | 11.6 | 72 | 178 | 46 | S07BB-F (450/750 V) — Heavy-duty +90 °C EPR/EPR flexible rubber
| S07BB-F 4G2.5 (450/750 V) | 450/750 V 4G2.5 | 2.5 | 12.8 | 96 | 222 | 51 | S07BB-F (450/750 V) — Heavy-duty +90 °C EPR/EPR flexible rubber
| S07BB-F 5G2.5 (450/750 V) | 450/750 V 5G2.5 | 2.5 | 14.2 | 120 | 272 | 57 | S07BB-F (450/750 V) — Heavy-duty +90 °C EPR/EPR flexible rubber
| S07BB-F 4G6.0 (450/750 V) | 450/750 V 4G6.0 | 6.0 | 16.8 | 230 | 430 | 67 | S07BB-F (450/750 V) — Heavy-duty +90 °C EPR/EPR flexible rubber
| S07BB-F 5G6.0 (450/750 V) | 450/750 V 5G6.0 | 6.0 | 18.6 | 288 | 530 | 74 | S07BB-F (450/750 V) — Heavy-duty +90 °C EPR/EPR flexible rubber
| S1BB-F 4G10 (0.6/1 kV) | 0.6/1 kV 4G10 | 10 | 21.6 | 384 | 730 | 86 | S1BB-F (0.6/1 kV) — Extra-heavy 1000 V +90 °C EPR/EPR flexible rubber
| S1BB-F 4G16 (0.6/1 kV) | 0.6/1 kV 4G16 | 16 | 24.8 | 614 | 1030 | 99 | S1BB-F (0.6/1 kV) — Extra-heavy 1000 V +90 °C EPR/EPR flexible rubber
| S1BB-F 4G25 (0.6/1 kV) | 0.6/1 kV 4G25 | 25 | 29.4 | 960 | 1520 | 118 | S1BB-F (0.6/1 kV) — Extra-heavy 1000 V +90 °C EPR/EPR flexible rubber
| S1BB-F 4G35 (0.6/1 kV) | 0.6/1 kV 4G35 | 35 | 33 | 1344 | 2010 | 132 | S1BB-F (0.6/1 kV) — Extra-heavy 1000 V +90 °C EPR/EPR flexible rubber
| S1BB-F 4G50 (0.6/1 kV) | 0.6/1 kV 4G50 | 50 | 38.2 | 1920 | 2760 | 153 | S1BB-F (0.6/1 kV) — Extra-heavy 1000 V +90 °C EPR/EPR flexible rubber
| S1BB-F 1×95 (0.6/1 kV) | 0.6/1 kV 1×95 | 95 | 22 | 912 | 1140 | 88 | S1BB-F (0.6/1 kV) — Extra-heavy 1000 V +90 °C EPR/EPR flexible rubber
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per EN 50525-2-21 / HD 361 / VDE 0285.

## Electrical & ampacity data
S07BB-F / S1BB-F Heavy-Duty EPR-Insulated Industrial Flexible – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07bb-f-s1bb-f-heavy-duty-epr-insulated-industrial-flexible-rubber-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
450/750 V 3G1.5 | 13.3 | 22 | 19 | 80 | 2500
450/750 V 3G2.5 | 7.98 | 30 | 26 | 82 | 2500
450/750 V 4G2.5 | 7.98 | 30 | 26 | 82 | 2500
450/750 V 5G2.5 | 7.98 | 30 | 26 | 82 | 2500
450/750 V 4G6.0 | 3.3 | 51 | 43 | 87 | 2500
450/750 V 5G6.0 | 3.3 | 51 | 43 | 87 | 2500
0.6/1 kV 4G10 | 1.91 | 70 | 60 | 92 | 2500
0.6/1 kV 4G16 | 1.21 | 93 | 79 | 101 | 2500
0.6/1 kV 4G25 | 0.78 | 123 | 105 | 114 | 2500
0.6/1 kV 4G35 | 0.554 | 152 | 129 | 129 | 2500
0.6/1 kV 4G50 | 0.386 | 189 | 161 | 150 | 2500
0.6/1 kV 1×95 | 0.206 | 282 | 240 | 216 | 2500
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
S07BB-F / S1BB-F Heavy-Duty EPR-Insulated Industrial Flexible – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07bb-f-s1bb-f-heavy-duty-epr-insulated-industrial-flexible-rubber-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 & 0.6/1 (S07BB-F (750 V) · S1BB-F (1000 V))
Key data | Conductor max. | +90 °C ('B') (Continuous · +250 °C short-circuit)
Key data | Cold flexibility | -40 °C mobile (-50 °C fixed · Superior to PCP)
Key data | Min. bend R | 4 × D / 6 × D (Fixed installation / mobile flexing)
Key data | Size range | 1.5–185 mm² (1-core to 24-core configurations)
Key data | Halogen status | 100 % Halogen-f (EN 60754-1/2 EPR insulation & sheath)
Electrical | Rated voltage (S07BB-F / S1BB-F) | 450/750 V AC / 0.6/1 kV AC
Electrical | Routine AC test voltage | 2.5 kV rms (S07) / 3.5 kV rms (S1)
Electrical | Specific volume resistivity | ≥ 10¹³ Ω·cm at +20 °C
Electrical | Conductor stranding class | EN 60228 Class 5
Electrical | Ampacity gain vs H07RN-F | +15 % to +18 % higher current rating
Electrical | Operating frequency | 50 / 60 Hz & DC
Thermal | Max. conductor operating temp. | +90 °C continuous ('B' EPR)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Mobile ambient range | -40 °C to +60 °C
Thermal | Fixed ambient range | -50 °C to +80 °C
Thermal | Min. laying temperature | -40 °C
Thermal | Thermal ageing resistance | EN 50363-1/2 EI7 & EM7 rated
Mechanical | Min. bend radius (fixed) | 4 × D (≤ 12 mm) / 5 × D (> 12 mm)
Mechanical | Min. bend radius (flexing) | 6 × D (≤ 12 mm) / 8 × D (> 12 mm)
Mechanical | Max. dynamic tensile pull | 15 N/mm² total copper cross-section
Mechanical | Cold-impact resilience | No cracking at -40 °C per EN 60811-506
Mechanical | Abrasion & tear resistance | Heavy-duty Type EM7 elastomer
Mechanical | Torsional stress (wind loop) | ±100 °/m in vertical drip loops
Resistance | Halogen-free & low corrosivity | EN 60754-1/2 (< 0.5 % halogens)
Resistance | Ozone & UV weather resistance | EN 60811-403 ozone-proof EPR
Resistance | Water & moisture resistance | Low water absorption EPR compound
Resistance | Sub-zero cold flexibility | Outperforms neoprene below -25 °C
Resistance | Chemical splash | Resistant to weak acids & alkalis
Resistance | RoHS / REACH status | CE & RoHS 3 compliant
Standards | Designation code system | CENELEC HD 361 S3 ('S07BB-F / S1BB-F')
Standards | Harmonised reference standard | EN 50525-2-21 (H07BB-F family)
Standards | Compound specification | EN 50363-1 (EI7) & EN 50363-2-1 (EM7)
Standards | Conductor standard | EN 60228 Class 5
Standards | Halogen test standard | EN 60754-1 / EN 60754-2
Standards | Quality certification | EN 10204 3.1 mill certificate
Identification | Core identification (≤ 5 cores) | HD 308 S2 colours (with G/Y)
Identification | Core identification (≥ 6 cores) | White numbers on black cores + G/Y
Identification | Outer sheath colour | Black
Identification | Surface marking | TEBAOFLEX S07BB-F / S1BB-F [n×mm²] +90C CE
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Lot number & year code

## Construction
S07BB-F / S1BB-F Heavy-Duty EPR-Insulated Industrial Flexible – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07bb-f-s1bb-f-heavy-duty-epr-insulated-industrial-flexible-rubber-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor ('-F') | Class 5 fine-stranded plain or tinned annealed copper wire | EN 60228 Class 5
2 | +90 °C EPR core insulation ('B') | Cross-linked ethylene-propylene elastomer Type EI7 (EN 50363-1) | EN 50363-1
3 | Short-pitch core lay-up | Cores stranded with short pitch and halogen-free elastomeric inner filling | EN 50525-2-21
4 | +90 °C EPR outer sheath ('B') | Heavy-duty cross-linked ethylene-propylene elastomer Type EM7, halogen-free, UV- and | EN 50363-2-1
| S07BB-F (450/750 V) | Halogen-free +90 °C EPR/EPR upgrade to H07RN-F for cold-climate and high-ampacity portable equipment.
| S1BB-F (0.6/1 kV) | Heavy-duty 0.6/1 kV +90 °C EPR/EPR power feeder for single-core and multi-core industrial distribution.

## Quality and supply
S07BB-F / S1BB-F Heavy-Duty EPR-Insulated Industrial Flexible – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07bb-f-s1bb-f-heavy-duty-epr-insulated-industrial-flexible-rubber-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage test — 2.5 kV rms (S07BB-F) or 3.5 kV rms (S1BB-F) for 5 minutes | Every drum
Routine test | Conductor DC resistance — Complies with EN 60228 Class 5 at 20 °C | Every drum
Sample test | -40 °C cold-bend & cold-impact test — No cracking of EM7 EPR sheath or EI7 insulation at -40 °C | Per batch
Type test | Halogen-free & +90 °C thermal ageing test — Passes EN 60754-1/2 halogen test and EN 50363-1/2 ageing | Type approval
Standard / approval | EN 50525-2-21 / HD 361
Standard / approval | EN 60754-1/2
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX S07BB-F / S1BB-F [n×mm²] +90C
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP