## Request a quote
Request a quotation for S07E6E5-F
Application engineer · submersible & chemical cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/s07e6e5-f-450-750v-fep-etfe-chemical-resistant-submersible-pump-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
S07E6E5-F 450/750 V FEP/ETFE Submersible Pump Cable – Dimensions, tensile ratings & weights (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07e6e5-f-450-750v-fep-etfe-chemical-resistant-submersible-pump-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on EN 50525 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Weight ≈ kg/km | Tensile load kN ≈ | Min. bend R mm | Series
| S07E6E5-F 4G6 + 2×1.5 mm² | 4G6 + 2×1.5 mm² | Class 5 Cu + FEP/ETFE | 16.4 | 485 | 3.2 | 135 | S07E6E5-F Construction Schedule (−50…+150 °C)
| S07E6E5-F 4G10 + 2×1.5 mm² | 4G10 + 2×1.5 mm² | Class 5 Cu + FEP/ETFE | 19.2 | 710 | 5 | 155 | S07E6E5-F Construction Schedule (−50…+150 °C)
| S07E6E5-F 4G16 + 2×1.5 mm² | 4G16 + 2×1.5 mm² | Class 5 Cu + FEP/ETFE | 22.5 | 1040 | 7.8 | 180 | S07E6E5-F Construction Schedule (−50…+150 °C)
| S07E6E5-F 4G25 + 2×1.5 mm² | 4G25 + 2×1.5 mm² | Class 5 Cu + FEP/ETFE | 26.8 | 1520 | 12 | 215 | S07E6E5-F Construction Schedule (−50…+150 °C)
Custom core counts, cross-sections, sheath colours and factory-tested cut lengths available per EN 50525 / IEC 60228 Class 5.

## Electrical, optical & thermal p
S07E6E5-F 450/750 V FEP/ETFE Submersible Pump Cable – Electrical, optical & thermal parameters (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07e6e5-f-450-750v-fep-etfe-chemical-resistant-submersible-pump-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on EN 50525 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Capacity | Operating temp.
4G6 + 2×1.5 mm² | 3.3 | 450/750 V / 52 A | −50…+150 °C
4G10 + 2×1.5 mm² | 1.91 | 450/750 V / 72 A | −50…+150 °C
4G16 + 2×1.5 mm² | 1.21 | 450/750 V / 96 A | −50…+150 °C
4G25 + 2×1.5 mm² | 0.78 | 450/750 V / 128 A | −50…+150 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric and dimensional verification.

## Technical data
S07E6E5-F 450/750 V FEP/ETFE Submersible Pump Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07e6e5-f-450-750v-fep-etfe-chemical-resistant-submersible-pump-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on EN 50525 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (Power cores + 2×pilot sensing cores)
Key data | Operating temp. | −50…+150 °C (Continuous thermal operating range)
Key data | Min. bend radius | 8–10 × OD (Installed / dynamic routing limit)
Key data | Core / conductor | Class 5 Cu (Power cores + 2×1.5 mm² pilot)
Key data | Outer protection | E5 FEP Jacket (Full fluoropolymer chemical sheath)
Key data | Standard | EN 50525 (EN 50525 / IEC 60228 Class 5)
Electrical | Rated voltage / transmission duty | 450/750 V (EN 50525 / IEC 60228 Class 5)
Electrical | Core / conductor construction | Power Conductors (4G16 mm²) — Class 5 finely stranded plain annealed copper power conductors (3 phase cores + 1 green/yellow protective earth core)
Electrical | Primary dielectric / insulation | Power Core Insulation (E6) — Extruded fluorinated ethylene propylene (FEP, code E6) primary insulation resistant to aggressive solvents, acids, and +180 °C media
Thermal | Continuous operating temperature | −50…+150 °C (rated operating envelope)
Thermal | Storage & transport temperature | −40…+80 °C on export drum or reel
Mechanical | Outer protection / sheath | Outer Sheath (E5) — Heavy-duty black fluorinated ethylene propylene (FEP, code E5) outer jacket impervious to hot Leachate, hydrocarbons, and corrosive chemicals
Mechanical | Minimum bending radius | 8–10 × OD
Mechanical | Structural layer count | 5 concentric functional layers
Resistance | Environmental & chemical resistance | Industrial moisture, oils and mechanical wear per EN 50525 / IEC 60228 Class 5
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | EN 50525 / IEC 60228 Class 5
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | S07E6E5-F
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
S07E6E5-F 450/750 V FEP/ETFE Submersible Pump Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07e6e5-f-450-750v-fep-etfe-chemical-resistant-submersible-pump-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on EN 50525 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Power Conductors (4G16 mm²) | Class 5 finely stranded plain annealed copper power conductors (3 phase cores + 1 green/yellow protective earth core) | EN 50525 / IEC 60228 Class 5
2 | Power Core Insulation (E6) | Extruded fluorinated ethylene propylene (FEP, code E6) primary insulation resistant to aggressive solvents, acids, and +180 °C media | EN 50525 / IEC 60228 Class 5
3 | Monitoring Conductors (2x1.5 mm²) | Two finely stranded plain copper auxiliary pilot conductors for submersible pump stator temperature and seal-leakage monitoring | EN 50525 / IEC 60228 Class 5
4 | Monitoring Core Insulation | High-mechanical-strength ethylene tetrafluoroethylene (ETFE) fluoropolymer insulation over the 2 x 1.5 mm² control cores | EN 50525 / IEC 60228 Class 5
5 | Outer Sheath (E5) | Heavy-duty black fluorinated ethylene propylene (FEP, code E5) outer jacket impervious to hot Leachate, hydrocarbons, and corrosive chemicals | EN 50525 / IEC 60228 Class 5
| S07E6E5-F — Standard Execution | Built to EN 50525 / IEC 60228 Class 5 with power conductors (4g16 mm²) and outer sheath (e5)
| S07E6E5-F — Custom Length & Configuration | Available in custom drum lengths, core counts or factory-terminated assemblies
| S07E6E5-F — Factory Routine Certified | Supplied with EN 10204 3.1 routine electrical, dielectric & dimensional inspection report

## Quality and supply
S07E6E5-F 450/750 V FEP/ETFE Submersible Pump Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07e6e5-f-450-750v-fep-etfe-chemical-resistant-submersible-pump-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on EN 50525 / IEC 60228 Class 5. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance & dimensional verification (EN 50525 / IEC 60228 Class 5) — Electrical parameters and outer diameter within EN 50525 / IEC 60228 Class 5 tolerances | Every manufactured drum / length
Routine test | High-voltage dielectric & insulation resistance test (EN 50525 / IEC 60228 Class 5) — Zero dielectric breakdown and verified insulation resistance over full length | Every manufactured drum / length
Type test | Thermal ageing, mechanical flexing & environmental qualification (EN 50525 / IEC 60228 Class 5) — Verified structural and dielectric integrity across −50…+150 °C | Type qualification & periodic lot audit
Standard / approval | EN 50525 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX S07E6E5-F EN 50525 450/750 V CE
Supply | Delivery form: Heavy-duty export wooden/steel drums or factory-tested coils
Supply | Standard lengths: 100 m, 250 m, 500 m, 1,000 m or custom cut-to-length reels
Supply | MOQ: 100 m (standard configurations) · 300 m (custom builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP