## Request a quote
Request a quotation for S07RC4N8-F
Specify core count (e.g. 4G for VFD pump motor or 7G–12G for pump control), conductor cross-section, submersion depth, and drum length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/s07rc4n8-f-screened-heavy-duty-submersible-polychloroprene-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
S07RC4N8-F Screened Heavy-Duty Submersible Polychloroprene Rubber – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07rc4n8-f-screened-heavy-duty-submersible-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| S07RC4N8-F 4G1.5 | 4G1.5 | 1.5 | 12.2 | 92 | 225 | 49 | Standard S07RC4N8-F configurations
| S07RC4N8-F 4G2.5 | 4G2.5 | 2.5 | 14.2 | 142 | 310 | 57 | Standard S07RC4N8-F configurations
| S07RC4N8-F 4G4.0 | 4G4.0 | 4.0 | 16.4 | 212 | 425 | 66 | Standard S07RC4N8-F configurations
| S07RC4N8-F 4G6.0 | 4G6.0 | 6.0 | 18.5 | 302 | 565 | 74 | Standard S07RC4N8-F configurations
| S07RC4N8-F 4G10 | 4G10 | 10 | 23.2 | 485 | 890 | 93 | Standard S07RC4N8-F configurations
| S07RC4N8-F 4G16 | 4G16 | 16 | 26.8 | 735 | 1250 | 107 | Standard S07RC4N8-F configurations
| S07RC4N8-F 4G25 | 4G25 | 25 | 31.6 | 1110 | 1810 | 126 | Standard S07RC4N8-F configurations
| S07RC4N8-F 4G35 | 4G35 | 35 | 35.2 | 1520 | 2360 | 141 | Standard S07RC4N8-F configurations
| S07RC4N8-F 7G1.5 | 7G1.5 | 1.5 | 15 | 148 | 340 | 60 | Standard S07RC4N8-F configurations
| S07RC4N8-F 12G1.5 | 12G1.5 | 1.5 | 19.2 | 240 | 530 | 77 | Standard S07RC4N8-F configurations
| S07RC4N8-F 7G2.5 | 7G2.5 | 2.5 | 17.6 | 235 | 490 | 70 | Standard S07RC4N8-F configurations
| S07RC4N8-F 12G2.5 | 12G2.5 | 2.5 | 22.4 | 385 | 765 | 90 | Standard S07RC4N8-F configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per EN 50525-2-21 AD8 / HD 361.

## Electrical & ampacity data
S07RC4N8-F Screened Heavy-Duty Submersible Polychloroprene Rubber – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07rc4n8-f-screened-heavy-duty-submersible-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
4G1.5 | 13.3 | 19 | 16 | 80 | 2500
4G2.5 | 7.98 | 26 | 22 | 82 | 2500
4G4.0 | 4.95 | 35 | 30 | 84 | 2500
4G6.0 | 3.3 | 45 | 38 | 87 | 2500
4G10 | 1.91 | 62 | 53 | 92 | 2500
4G16 | 1.21 | 83 | 71 | 101 | 2500
4G25 | 0.78 | 109 | 93 | 114 | 2500
4G35 | 0.554 | 135 | 115 | 129 | 2500
7G1.5 | 13.3 | 19 | 16 | 80 | 2500
12G1.5 | 13.3 | 19 | 16 | 80 | 2500
7G2.5 | 7.98 | 26 | 22 | 82 | 2500
12G2.5 | 7.98 | 26 | 22 | 82 | 2500
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
S07RC4N8-F Screened Heavy-Duty Submersible Polychloroprene Rubber – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07rc4n8-f-screened-heavy-duty-submersible-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (U0/U AC · Submersible pump & control)
Key data | Water class | AD8 Submersion (Permanent immersion to 10–100 m)
Key data | EMC screening | Tinned Cu 'C4' (≥ 85 % braid for VFD & sensors)
Key data | Conductor max. | +60 °C (+85 °C) (+40 °C water / +85 °C in air)
Key data | Min. bend R | 4 × D / 6 × D (Fixed submerged / pump hoisting)
Key data | Outer sheath | EM2 AD8 PCP 'N8' (Oil-, sewage- & flame-retardant)
Electrical | Rated voltage U0/U | 450/750 V AC
Electrical | Routine AC test voltage | 2.5 kV rms / 5 min
Electrical | Screen optical coverage ('C4') | ≥ 85 % tinned copper wire braid
Electrical | Wet insulation resistance | Stable under AD8 immersion
Electrical | Conductor stranding class | EN 60228 Class 5
Electrical | Operating frequency | 50 / 60 Hz & VFD PWM
Thermal | Max. water temperature (AD8) | +40 °C continuous submersion
Thermal | Max. conductor temp. (in air) | +60 °C (EN 50525-2-21) / +85 °C EPR
Thermal | Max. short-circuit temperature | +200 °C (max. 5 s)
Thermal | Mobile ambient range (in air) | -25 °C to +60 °C
Thermal | Fixed ambient range (in air) | -40 °C to +60 °C
Thermal | Min. installation temperature | -25 °C
Mechanical | Min. bend radius (fixed) | 4 × D (≤ 12 mm) / 5 × D (> 12 mm)
Mechanical | Min. bend radius (flexing) | 6 × D (≤ 12 mm) / 8 × D (> 12 mm)
Mechanical | Max. submersion depth | 10 m (EN 50525-2-21) / up to 100 m factory
Mechanical | Max. tensile pull on copper | 15 N/mm²
Mechanical | Crush & abrasion resistance | Heavy-duty EM2 polychloroprene
Mechanical | Gland termination | 360° EMC compression gland compatible
Resistance | AD8 permanent water immersion | EN 50525-2-21 Annex D/E certified
Resistance | Oil, grease & sewage sludge | EN 60811-404 oil-resistant EM2 PCP
Resistance | Flame retardance | EN 60332-1-2 self-extinguishing
Resistance | Ozone & UV weather resistance | EN 60811-403 ozone-proof
Resistance | EMC interference immunity | Shielded against VFD common-mode currents
Resistance | Halogen status | Polychloroprene elastomer
Standards | Designation code system | CENELEC HD 361 S3 ('S07RC4N8-F')
Standards | Submersible reference norm | EN 50525-2-21 (H07RN8-F AD8 family)
Standards | Compound standard | EN 50363-1 (EI4) & EN 50363-2-1 (EM2)
Standards | Conductor standard | EN 60228 Class 5
Standards | Flame test standard | EN 60332-1-2
Standards | Quality certification | EN 10204 3.1 mill certificate
Identification | Core identification (≤ 5 cores) | HD 308 S2 colours (with G/Y)
Identification | Core identification (≥ 6 cores) | White numbers on black cores + G/Y
Identification | Outer sheath colour | Black
Identification | Surface marking | TEBAOFLEX S07RC4N8-F [n×mm²] AD8 CE
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Lot number & year code

## Construction
S07RC4N8-F Screened Heavy-Duty Submersible Polychloroprene Rubber – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07rc4n8-f-screened-heavy-duty-submersible-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor ('-F') | Class 5 fine-stranded plain or tinned annealed copper wire | EN 60228 Class 5
2 | Water-resistant EPR insulation ('R') | Cross-linked ethylene-propylene elastomer Type EI4 formulated for AD8 low water absorption | EN 50363-1 / EN 50525-2-21
3 | Water-blocking inner elastomer bedding | Extruded rubber inner covering filling core interstices beneath the metallic screen | EN 50525-2-21
4 | Tinned copper wire braid screen ('C4') | Braided tin-coated copper wires (≥ 85 % optical coverage) providing 360° EMC shielding | HD 361 S3
5 | AD8 submersible polychloroprene sheath | Heavy-duty flame-retardant, oil- and sewage-resistant polychloroprene compound Type EM2 | EN 50363-2-1 / EN 50525-2-21
| S07RC4N8-F Power (4G1.5–4G50) | Screened 4-core (3+PE) submersible pump motor feeder for inverter-driven wet-well and dewatering pumps.
| S07RC4N8-F Control (7G1.5–18G2.5) | Screened multi-core submersible control and thermal/moisture sensor cable for large pump units.

## Quality and supply
S07RC4N8-F Screened Heavy-Duty Submersible Polychloroprene Rubber – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/s07rc4n8-f-screened-heavy-duty-submersible-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC water-bath dielectric test — 2.5 kV rms for 5 minutes without breakdown | Every drum
Routine test | Conductor & C4 braid DC resistance — EN 60228 Class 5 & ≥ 85 % tinned copper braid verified | Every drum
Sample test | AD8 gravimetric water absorption test — Complies with EN 50525-2-21 Annex D/E water immersion limits | Per batch
Type test | Oil immersion & vertical flame test — Passes EN 60811-404 oil test and EN 60332-1-2 flame test | Type approval
Standard / approval | EN 50525-2-21 AD8 / HD 361
Standard / approval | EN 60332-1-2
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX S07RC4N8-F 450/750V [n×mm²] AD8
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP