## Request a quote
Request a quotation for S1BC4N8-F
Specify core configuration (4G or symmetrical 3×+3G), phase cross-section (2.5 to 120 mm²), VFD operating voltage (400 V or 690 V), and submersion depth.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/s1bc4n8-f-0-6-1-kv-screened-heavy-duty-submersible-industrial-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
S1BC4N8-F 0.6/1 kV Screened Heavy-Duty Submersible & Industrial – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bc4n8-f-0-6-1-kv-screened-heavy-duty-submersible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| S1BC4N8-F 4G2.5 | 4G2.5 | 2.5 | 15 | 146 | 345 | 75 | Standard S1BC4N8-F configurations
| S1BC4N8-F 4G4.0 | 4G4.0 | 4.0 | 17.2 | 218 | 465 | 86 | Standard S1BC4N8-F configurations
| S1BC4N8-F 4G6.0 | 4G6.0 | 6.0 | 19.4 | 310 | 615 | 97 | Standard S1BC4N8-F configurations
| S1BC4N8-F 4G10 | 4G10 | 10 | 24.2 | 495 | 960 | 121 | Standard S1BC4N8-F configurations
| S1BC4N8-F 4G16 | 4G16 | 16 | 27.8 | 748 | 1340 | 139 | Standard S1BC4N8-F configurations
| S1BC4N8-F 4G25 | 4G25 | 25 | 32.8 | 1125 | 1940 | 164 | Standard S1BC4N8-F configurations
| S1BC4N8-F 4G35 | 4G35 | 35 | 36.5 | 1540 | 2520 | 182 | Standard S1BC4N8-F configurations
| S1BC4N8-F 4G50 | 4G50 | 50 | 42 | 2160 | 3460 | 210 | Standard S1BC4N8-F configurations
| S1BC4N8-F 4G70 | 4G70 | 70 | 47.5 | 2980 | 4610 | 238 | Standard S1BC4N8-F configurations
| S1BC4N8-F 4G95 | 4G95 | 95 | 53.6 | 4010 | 5980 | 268 | Standard S1BC4N8-F configurations
| S1BC4N8-F 7G2.5 | 7G2.5 | 2.5 | 18.6 | 242 | 540 | 93 | Standard S1BC4N8-F configurations
| S1BC4N8-F 12G2.5 | 12G2.5 | 2.5 | 23.6 | 395 | 835 | 118 | Standard S1BC4N8-F configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per EN 50525-2-21 AD8 / HD 361 / VDE 0285.

## Electrical & ampacity data
S1BC4N8-F 0.6/1 kV Screened Heavy-Duty Submersible & Industrial – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bc4n8-f-0-6-1-kv-screened-heavy-duty-submersible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
4G2.5 | 7.98 | 30 | 26 | 82 | 3500
4G4.0 | 4.95 | 40 | 34 | 84 | 3500
4G6.0 | 3.3 | 51 | 43 | 87 | 3500
4G10 | 1.91 | 70 | 60 | 92 | 3500
4G16 | 1.21 | 93 | 79 | 101 | 3500
4G25 | 0.78 | 123 | 105 | 114 | 3500
4G35 | 0.554 | 152 | 129 | 129 | 3500
4G50 | 0.386 | 189 | 161 | 150 | 3500
4G70 | 0.272 | 233 | 198 | 180 | 3500
4G95 | 0.206 | 282 | 240 | 216 | 3500
7G2.5 | 7.98 | 30 | 26 | 82 | 3500
12G2.5 | 7.98 | 30 | 26 | 82 | 3500
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
S1BC4N8-F 0.6/1 kV Screened Heavy-Duty Submersible & Industrial – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bc4n8-f-0-6-1-kv-screened-heavy-duty-submersible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV AC (U0/U ('S1') · 1.5 kV DC)
Key data | Water class | AD8 Submersion (Permanent immersion up to 100 m)
Key data | EMC screening | Tinned Cu 'C4' (≥ 85 % braid for 690 V/1000 V VFDs)
Key data | Conductor max. | +90 °C ('B') (High-ampacity EPR · +250 °C SC)
Key data | Min. bend R | 5 × D / 8 × D (Fixed installation / mobile flexing)
Key data | Outer sheath | EM2 AD8 PCP 'N8' (Oil-, sewage- & flame-retardant)
Electrical | Rated voltage U0/U | 0.6/1 kV AC (Um 1.2 kV)
Electrical | Routine AC test voltage | 3.5 kV rms / 5 min
Electrical | Screen optical coverage ('C4') | ≥ 85 % tinned copper wire braid
Electrical | VFD system compatibility | 400 V & 690 V PWM inverter drives
Electrical | Conductor stranding class | EN 60228 Class 5
Electrical | Specific insulation resistance | ≥ 500 MΩ·km at +20 °C
Thermal | Max. conductor temp. (in air) | +90 °C continuous ('B' EPR)
Thermal | Max. water temperature (AD8) | +40 °C (+50 °C short-term)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Mobile ambient range (in air) | -25 °C to +60 °C
Thermal | Fixed ambient range (in air) | -40 °C to +80 °C
Thermal | Current rating advantage | +15 % higher ampacity vs S07RC4N8-F
Mechanical | Min. bend radius (fixed) | 5 × overall diameter (D)
Mechanical | Min. bend radius (flexing) | 8 × overall diameter (D)
Mechanical | Max. submersion depth (AD8) | Up to 100 m water head (10 bar)
Mechanical | Max. tensile pull on copper | 15 N/mm²
Mechanical | Crush & abrasion resistance | Heavy-duty 0.6/1 kV EM2 PCP
Mechanical | Gland termination | 360° EMC submersible cable entry
Resistance | AD8 permanent water immersion | EN 50525-2-21 Annex D/E certified
Resistance | Oil, diesel & sewage sludge | EN 60811-404 oil-resistant EM2 PCP
Resistance | Flame retardance | EN 60332-1-2 self-extinguishing
Resistance | Ozone & UV weather resistance | EN 60811-403 ozone-proof
Resistance | EMC & bearing-current mitigation | Low-impedance 'C4' tinned Cu braid
Resistance | Halogen status | Polychloroprene outer sheath
Standards | Designation code system | CENELEC HD 361 S3 ('S1BC4N8-F')
Standards | Submersible design basis | EN 50525-2-21 AD8 & DIN VDE 0285
Standards | Compound standard | EN 50363-1 (EI7) & EN 50363-2-1 (EM2)
Standards | Conductor standard | EN 60228 Class 5
Standards | Flame test standard | EN 60332-1-2
Standards | Quality certification | EN 10204 3.1 mill certificate
Identification | Core identification (≤ 5 cores) | HD 308 S2 colours (with G/Y)
Identification | Core identification (≥ 6 cores) | White numbers on black cores + G/Y
Identification | Outer sheath colour | Black
Identification | Surface marking | TEBAOFLEX S1BC4N8-F 0.6/1kV [n×mm²] AD8 CE
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Lot number & year code

## Construction
S1BC4N8-F 0.6/1 kV Screened Heavy-Duty Submersible & Industrial – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bc4n8-f-0-6-1-kv-screened-heavy-duty-submersible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor ('-F') | Class 5 fine-stranded plain or tinned annealed copper wire | EN 60228 Class 5
2 | 0.6/1 kV +90 °C EPR insulation ('1B') | Cross-linked ethylene-propylene elastomer Type EI7 / 3GI3 with low water absorption and | EN 50363-1
3 | Extruded elastomeric inner sheath | Water-blocking rubber inner bedding filling core interstices under the copper braid | EN 50525-2-21
4 | Tinned copper wire braid screen ('C4') | Braided tin-coated copper wires with ≥ 85 % optical coverage for low-impedance VFD EMC | HD 361 S3
5 | AD8 submersible polychloroprene sheath | Heavy-duty flame-retardant, oil-, sewage-, and tear-resistant polychloroprene compound | EN 50363-2-1 / EN 50525-2-21
| S1BC4N8-F 4G (2.5–120 mm²) | Screened 0.6/1 kV 4-core (3+PE) power feeder for 400 V / 690 V VFD-driven submersible pumps and wet drives.
| S1BC4N8-F 3×+3G (Symmetrical VFD) | Three phase cores plus three split earth cores inside the C4 copper braid for large ≥ 35 mm² VFD pump motors.

## Quality and supply
S1BC4N8-F 0.6/1 kV Screened Heavy-Duty Submersible & Industrial – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bc4n8-f-0-6-1-kv-screened-heavy-duty-submersible-industrial-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 0.6/1 kV AC dielectric voltage test — 3.5 kV rms for 5 minutes without breakdown | Every drum
Routine test | Conductor & C4 braid DC resistance — EN 60228 Class 5 & ≥ 85 % tinned copper braid verified | Every drum
Sample test | AD8 water immersion & +90 °C thermal ageing — Passes EN 50525-2-21 Annex D/E water uptake and EI7 ageing | Per batch
Type test | Hydrostatic 10 bar submersion & oil test — Passes 100 m water pressure test, EN 60811-404 oil & EN 60332-1-2 | Type approval
Standard / approval | EN 50525-2-21 AD8 / HD 361
Standard / approval | EN 60332-1-2
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX S1BC4N8-F 0.6/1kV [n×mm²] +90C
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP