## Request a quote
Request a quotation for S1BN8-F
Specify core configuration (single-core 1× or multi-core 3G, 4G, 5G, 7G), conductor cross-section (1.5 to 185 mm²), and submersion depth.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/s1bn8-f-0-6-1-kv-heavy-duty-submersible-industrial-polychloroprene-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
S1BN8-F 0.6/1 kV Heavy-Duty Submersible & Industrial – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bn8-f-0-6-1-kv-heavy-duty-submersible-industrial-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| S1BN8-F 3G2.5 | 3G2.5 | 2.5 | 12.2 | 72 | 205 | 49 | Standard S1BN8-F configurations
| S1BN8-F 4G2.5 | 4G2.5 | 2.5 | 13.5 | 96 | 258 | 54 | Standard S1BN8-F configurations
| S1BN8-F 4G4.0 | 4G4.0 | 4.0 | 15.6 | 154 | 362 | 62 | Standard S1BN8-F configurations
| S1BN8-F 4G6.0 | 4G6.0 | 6.0 | 17.6 | 230 | 485 | 70 | Standard S1BN8-F configurations
| S1BN8-F 4G10 | 4G10 | 10 | 22.4 | 384 | 795 | 90 | Standard S1BN8-F configurations
| S1BN8-F 4G16 | 4G16 | 16 | 25.8 | 614 | 1120 | 103 | Standard S1BN8-F configurations
| S1BN8-F 4G25 | 4G25 | 25 | 30.6 | 960 | 1650 | 122 | Standard S1BN8-F configurations
| S1BN8-F 4G35 | 4G35 | 35 | 34.2 | 1344 | 2180 | 137 | Standard S1BN8-F configurations
| S1BN8-F 4G50 | 4G50 | 50 | 39.6 | 1920 | 3020 | 158 | Standard S1BN8-F configurations
| S1BN8-F 4G70 | 4G70 | 70 | 44.8 | 2688 | 4050 | 179 | Standard S1BN8-F configurations
| S1BN8-F 1×95 | 1×95 | 95 | 22.8 | 912 | 1210 | 91 | Standard S1BN8-F configurations
| S1BN8-F 1×150 | 1×150 | 150 | 27.2 | 1440 | 1820 | 109 | Standard S1BN8-F configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per EN 50525-2-21 AD8 / HD 361 / VDE 0285.

## Electrical & ampacity data
S1BN8-F 0.6/1 kV Heavy-Duty Submersible & Industrial – Electrical & ampacity data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bn8-f-0-6-1-kv-heavy-duty-submersible-industrial-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
3G2.5 | 7.98 | 30 | 26 | 82 | 3500
4G2.5 | 7.98 | 30 | 26 | 82 | 3500
4G4.0 | 4.95 | 40 | 34 | 84 | 3500
4G6.0 | 3.3 | 51 | 43 | 87 | 3500
4G10 | 1.91 | 70 | 60 | 92 | 3500
4G16 | 1.21 | 93 | 79 | 101 | 3500
4G25 | 0.78 | 123 | 105 | 114 | 3500
4G35 | 0.554 | 152 | 129 | 129 | 3500
4G50 | 0.386 | 189 | 161 | 150 | 3500
4G70 | 0.272 | 233 | 198 | 180 | 3500
1×95 | 0.206 | 282 | 240 | 216 | 3500
1×150 | 0.129 | 374 | 318 | 268 | 3500
Current ratings apply at +25/+30 °C ambient in free air; apply standard derating factors for elevated ambient or drum coiling.

## Technical data
S1BN8-F 0.6/1 kV Heavy-Duty Submersible & Industrial – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bn8-f-0-6-1-kv-heavy-duty-submersible-industrial-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV AC (U0/U ('S1') · 1.5 kV DC)
Key data | Water class | AD8 Submersion (Permanent immersion up to 100 m)
Key data | Conductor max. | +90 °C ('B') (Heat-resistant EPR · +250 °C SC)
Key data | Min. bend R | 4 × D / 6 × D (Fixed submerged / mobile flexing)
Key data | Size range | 1.5–185 mm² (Single-core & multi-core feeders)
Key data | Outer sheath | EM2 AD8 PCP 'N8' (Oil-, sewage- & flame-retardant)
Electrical | Rated voltage U0/U | 0.6/1 kV AC (Um 1.2 kV)
Electrical | Routine AC test voltage | 3.5 kV rms / 5 min
Electrical | Wet insulation resistance | ≥ 500 MΩ·km at +20 °C
Electrical | Conductor stranding class | EN 60228 Class 5
Electrical | Ampacity gain vs H07RN8-F | +15 % to +18 % higher current rating
Electrical | Operating frequency | 50 / 60 Hz & DC
Thermal | Max. conductor temp. (in air) | +90 °C continuous ('B' EPR)
Thermal | Max. water temperature (AD8) | +40 °C continuous (+50 °C peak)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s)
Thermal | Mobile ambient range (in air) | -25 °C to +60 °C
Thermal | Fixed ambient range (in air) | -40 °C to +80 °C
Thermal | Min. installation temperature | -25 °C
Mechanical | Min. bend radius (fixed) | 4 × D (≤ 12 mm) / 5 × D (> 12 mm)
Mechanical | Min. bend radius (flexing) | 6 × D (≤ 12 mm) / 8 × D (> 12 mm)
Mechanical | Max. submersion depth (AD8) | Up to 100 m water head (10 bar)
Mechanical | Max. tensile pull on copper | 15 N/mm²
Mechanical | Crush & abrasion resistance | Heavy-duty EM2 polychloroprene
Mechanical | Tear strength | ≥ 15 N/mm
Resistance | AD8 permanent water immersion | EN 50525-2-21 Annex D/E certified
Resistance | Oil, grease & sewage sludge | EN 60811-404 oil-resistant EM2 PCP
Resistance | Flame retardance | EN 60332-1-2 self-extinguishing
Resistance | Ozone & UV weather resistance | EN 60811-403 ozone-proof
Resistance | Chemical & slurry exposure | Resistant to pH 4–10 wastewater
Resistance | Halogen status | Polychloroprene elastomer
Standards | Designation code system | CENELEC HD 361 S3 ('S1BN8-F')
Standards | Submersible reference norm | EN 50525-2-21 (H07RN8-F AD8 family)
Standards | Compound standard | EN 50363-1 (EI7) & EN 50363-2-1 (EM2)
Standards | Conductor standard | EN 60228 Class 5
Standards | Flame test standard | EN 60332-1-2
Standards | Quality certification | EN 10204 3.1 mill certificate
Identification | Core identification (≤ 5 cores) | HD 308 S2 colours (with G/Y)
Identification | Core identification (≥ 6 cores) | White numbers on black cores + G/Y
Identification | Outer sheath colour | Black
Identification | Surface marking | TEBAOFLEX S1BN8-F 0.6/1kV [n×mm²] +90C AD8 CE
Identification | Length marking | Sequential metre marking
Identification | Batch traceability | Lot number & year code

## Construction
S1BN8-F 0.6/1 kV Heavy-Duty Submersible & Industrial – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bn8-f-0-6-1-kv-heavy-duty-submersible-industrial-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor ('-F') | Class 5 fine-stranded plain or tinned annealed copper wire | EN 60228 Class 5
2 | 0.6/1 kV +90 °C EPR insulation ('1B') | Cross-linked ethylene-propylene elastomer Type EI7 / 3GI3 engineered for +90 °C rating | EN 50363-1
3 | Short-pitch water-resistant core lay-up | Cores stranded with tight pitch and hydrophobic elastomeric interstices | EN 50525-2-21
4 | AD8 submersible polychloroprene sheath | Heavy-duty flame-retardant, oil-, sewage-, and abrasion-resistant polychloroprene | EN 50363-2-1 / EN 50525-2-21
| S1BN8-F Multi-Core (3G to 5G, 7G–18G) | 0.6/1 kV three-phase power and control risers for DOL and star-delta submersible pumps (1.5–120 mm²).
| S1BN8-F Single-Core (1×25 to 1×185 mm²) | High-current 0.6/1 kV single-core submersible leads for large axial-flow flood pumps and dewatering stations.

## Quality and supply
S1BN8-F 0.6/1 kV Heavy-Duty Submersible & Industrial – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bn8-f-0-6-1-kv-heavy-duty-submersible-industrial-polychloroprene-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / HD 361 / VDE 0285. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 0.6/1 kV AC dielectric voltage test — 3.5 kV rms for 5 minutes without breakdown | Every drum
Routine test | Conductor DC resistance — Complies with EN 60228 Class 5 at 20 °C | Every drum
Sample test | AD8 gravimetric water absorption & +90 °C ageing — Passes EN 50525-2-21 Annex D/E water test and EI7 ageing | Per batch
Type test | 10 bar hydrostatic submersion & oil test — Passes 100 m water pressure test, EN 60811-404 oil & EN 60332-1-2 | Type approval
Standard / approval | EN 50525-2-21 AD8 / HD 361
Standard / approval | EN 60332-1-2
Standard / approval | CE / RoHS
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX S1BN8-F 0.6/1kV [n×mm²] +90C AD8
Supply | Delivery form: Fumigated export wooden drums or coils
Supply | Standard drum lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP