## Request a quote
Request a quotation for S1BZ-F & VSCCB
Share inverter power rating, immersion depth, phase cross-section and EMC earthing gland requirements.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/s1bz-f-vsccb/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
S1BZ-F (2,000m HF) & VSCCB (500m EMC Screened) 0.6/1 kV Pump Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bz-f-vsccb/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| S1BZ-F 4G16 mm² | 4G16 mm² (3×16 + 1G16) | IEC 60228 Class 5 flexible Cu/SnCu | 21.8 | 840 | 2.4 | 130 | S1BZ-F & VSCCB Construction Schedule (−25…+90 °C)
| S1BZ-F 4G35 mm² | 4G35 mm² (3×35 + 1G16) | IEC 60228 Class 5 flexible Cu/SnCu | 28.6 | 1620 | 5.2 | 172 | S1BZ-F & VSCCB Construction Schedule (−25…+90 °C)
| S1BZ-F 3×70 + 3G16 mm² | 3 × 70 mm² + 3G16 mm² | IEC 60228 Class 5 flexible Cu/SnCu | 38.4 | 3180 | 10.5 | 230 | S1BZ-F & VSCCB Construction Schedule (−25…+90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable.

## Electrical, optical & thermal p
S1BZ-F (2,000m HF) & VSCCB (500m EMC Screened) 0.6/1 kV Pump Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bz-f-vsccb/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
4G16 mm² (3×16 + 1G16) | 1.21 | 0.6/1 kV (94 A submerged) | −25…+90 °C
4G35 mm² (3×35 + 1G16) | 0.554 | 0.6/1 kV (152 A submerged) | −25…+90 °C
3 × 70 mm² + 3G16 mm² | 0.272 | 0.6/1 kV (235 A submerged) | −25…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
S1BZ-F (2,000m HF) & VSCCB (500m EMC Screened) 0.6/1 kV Pump Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bz-f-vsccb/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Tested per VDE 0282 / EMC VFD)
Key data | Operating temp. | −25…+90 °C (Continuous subsea & marine service)
Key data | Min. bend radius | 6 × OD (Dynamic sheave & fixed routing)
Key data | Core / conductor | 3–4G 1.5–240 mm² (Class 5 bare/SnCu + HEPR)
Key data | Outer protection | HF EVA/SnCu+EPR (Halogen-free EVA or SnCu braid + EPR)
Key data | Standard | VDE 0282/EMC VFD (DIN VDE 0282)
Electrical | Rated voltage / transmission duty | 0.6/1 kV (DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable)
Electrical | Core / conductor construction | Class 5 Copper Conductors (Up to 240 mm²) — Finely stranded plain copper (S1BZ-F) or tinned copper ≤6 mm² (VSCCB EMC Screened)
Electrical | Primary dielectric / buffering | 0.6/1 kV HEPR / EPR Core Insulation — Reduced-wall HEPR (S1BZ-F 0.6/1 kV) or EPR (VSCCB EMC Screened) rated +90 °C
Thermal | Continuous operating temperature | −25…+90 °C (subsea, marine & submersible duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Tinned Copper Braid & Oil-Resistant Sheath — Tinned Cu braid (VSCCB) + halogen-free oil-resistant EVA (2,000 m) or EPR (500 m) jacket
Mechanical | Minimum bending radius | 6 × OD
Mechanical | Hydrostatic, tensile & crush duty | Waterproof Anti-Bubble Inner Sheath — Special EPDM / EPR inner sheath preventing osmotic water-bubble formation under pressure
Resistance | Hydrostatic pressure & water blocking | Engineered for continuous submersion and hydrostatic integrity per DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable
Resistance | Seawater, oil & chemical resistance | Resistant to seawater hydrolysis, hydraulic oils and abrasion per DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable
Standards | Environmental & test standards | IEC 60228 / IEC 60332 / ISO 13628-5 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | S1BZ-F & VSCCB
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (HF EVA (2km) / SnCu+EPR)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
S1BZ-F (2,000m HF) & VSCCB (500m EMC Screened) 0.6/1 kV Pump Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bz-f-vsccb/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 Copper Conductors (Up to 240 mm²) | Finely stranded plain copper (S1BZ-F) or tinned copper ≤6 mm² (VSCCB EMC Screened)
2 | 0.6/1 kV HEPR / EPR Core Insulation | Reduced-wall HEPR (S1BZ-F 0.6/1 kV) or EPR (VSCCB EMC Screened) rated +90 °C
3 | Waterproof Anti-Bubble Inner Sheath | Special EPDM / EPR inner sheath preventing osmotic water-bubble formation under pressure
4 | Tinned Copper Braid & Oil-Resistant Sheath | Tinned Cu braid (VSCCB) + halogen-free oil-resistant EVA (2,000 m) or EPR (500 m) jacket
| S1BZ-F & VSCCB — Standard Subsea & Marine Execution | Built to DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable with class 5 copper conductors (up to 240 mm²) and tinned copper braid & oil-resistant sheath
| S1BZ-F & VSCCB — Custom Drum Length & Termination Kit | Available in custom continuous subsea/wellbore drum lengths or pre-terminated assemblies
| S1BZ-F & VSCCB — Routine & Hydrostatic Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & pressure/dimensional report

## Quality and supply
S1BZ-F (2,000m HF) & VSCCB (500m EMC Screened) 0.6/1 kV Pump Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1bz-f-vsccb/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable) — DC resistance at 20 °C / optical attenuation and outer diameter within DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable) — Zero dielectric breakdown and verified insulation resistance for 0.6/1 kV rating | Every manufactured drum length
Type test | Hydrostatic pressure, water-blocking & mechanical endurance qualification (DIN VDE 0282 / IEC 60811-404 2,000m HF & EMC Pump Cable) — Verified submersion integrity, tensile load and thermal stability across −25…+90 °C | Type qualification & periodic lot audit
Standard / approval | VDE 0282 / EMC VFD Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX S1BZ-F & VSCCB VDE 0282 / EMC VFD 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel subsea reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous subsea/wellbore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP