## Request a quote
Request a quotation for S1RN8-F / S1RC4N8-F & S1BNH2-F
Share immersion depth (AD8), pump motor kW/voltage, water medium (potable/sewage/thermal) and required cut lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/s1rn8-f-s1rc4n8-f-s1bnh2-f/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
S1RN8-F / S1RC4N8-F & S1BNH2-F 0.6/1 kV 3GI3/EM2 Submersible Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1rn8-f-s1rc4n8-f-s1bnh2-f/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| S1RN8-F 4G16 mm² | 4G16 mm² (3×16 + 1G16) | IEC 60228 Class 5 flexible Cu/SnCu | 21.8 | 840 | 2.4 | 130 | S1RN8-F / S1RC4N8-F & S1BNH2-F Construction Schedule (−25…+80 °C)
| S1RN8-F 4G35 mm² | 4G35 mm² (3×35 + 1G16) | IEC 60228 Class 5 flexible Cu/SnCu | 28.6 | 1620 | 5.2 | 172 | S1RN8-F / S1RC4N8-F & S1BNH2-F Construction Schedule (−25…+80 °C)
| S1RN8-F 3×70 + 3G16 mm² | 3 × 70 mm² + 3G16 mm² | IEC 60228 Class 5 flexible Cu/SnCu | 38.4 | 3180 | 10.5 | 230 | S1RN8-F / S1RC4N8-F & S1BNH2-F Construction Schedule (−25…+80 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard.

## Electrical, optical & thermal p
S1RN8-F / S1RC4N8-F & S1BNH2-F 0.6/1 kV 3GI3/EM2 Submersible Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1rn8-f-s1rc4n8-f-s1bnh2-f/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
4G16 mm² (3×16 + 1G16) | 1.21 | 0.6/1 kV (94 A submerged) | −25…+80 °C
4G35 mm² (3×35 + 1G16) | 0.554 | 0.6/1 kV (152 A submerged) | −25…+80 °C
3 × 70 mm² + 3G16 mm² | 0.272 | 0.6/1 kV (235 A submerged) | −25…+80 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
S1RN8-F / S1RC4N8-F & S1BNH2-F 0.6/1 kV 3GI3/EM2 Submersible Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1rn8-f-s1rc4n8-f-s1bnh2-f/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Tested per VDE 0207-20 / EN 50363)
Key data | Operating temp. | −25…+80 °C (Continuous subsea & marine service)
Key data | Min. bend radius | 6 × OD (Dynamic sheave & fixed routing)
Key data | Core / conductor | 3G–4G 1.5–185 (Class 5 bare or SnCu+3GI3 EPR insulation)
Key data | Outer protection | Black EM2 (EN 50363-2-1 EM2 synthetic rubber)
Key data | Standard | VDE 0207-20 (VDE 0207-20 3GI3 & EN 50363-2-1 EM2)
Electrical | Rated voltage / transmission duty | 0.6/1 kV (VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard)
Electrical | Core / conductor construction | Class 5 Copper Conductors (Bare / Tinned) — Class 5 bare Cu (S1RN8-F / S1RC4N8-F) or parallel tinned Cu in 300 m S1BNH2-F Flat Submersible
Electrical | Primary dielectric / buffering | 3GI3 Grade EPR Core Insulation (0.6/1 kV) — VDE 0207-20 3GI3 cross-linked ethylene propylene rubber (4.0 kV test, +90 °C)
Thermal | Continuous operating temperature | −25…+80 °C (subsea, marine & submersible duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Black EM2 Submersible Elastomer Sheath — EN 50363-2-1 EM2 synthetic rubber jacket for 100 m (round) to 300 m (Flat Submersible) depth
Mechanical | Minimum bending radius | 6 × OD
Mechanical | Hydrostatic, tensile & crush duty | Rubber Inner Sheath & Bare Copper Braid (C4) — Extruded rubber inner sheath + bare copper wire braid screen on S1RC4N8-F SUBMERSIBLE S
Resistance | Hydrostatic pressure & water blocking | Engineered for continuous submersion and hydrostatic integrity per VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard
Resistance | Seawater, oil & chemical resistance | Resistant to seawater hydrolysis, hydraulic oils and abrasion per VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard
Standards | Environmental & test standards | IEC 60228 / IEC 60332 / ISO 13628-5 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | S1RN8-F / S1RC4N8-F & S1BNH2-F
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Black EM2 Elastomer)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
S1RN8-F / S1RC4N8-F & S1BNH2-F 0.6/1 kV 3GI3/EM2 Submersible Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1rn8-f-s1rc4n8-f-s1bnh2-f/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 Copper Conductors (Bare / Tinned) | Class 5 bare Cu (S1RN8-F / S1RC4N8-F) or parallel tinned Cu in 300 m S1BNH2-F Flat Submersible
2 | 3GI3 Grade EPR Core Insulation (0.6/1 kV) | VDE 0207-20 3GI3 cross-linked ethylene propylene rubber (4.0 kV test, +90 °C)
3 | Rubber Inner Sheath & Bare Copper Braid (C4) | Extruded rubber inner sheath + bare copper wire braid screen on S1RC4N8-F SUBMERSIBLE S
4 | Black EM2 Submersible Elastomer Sheath | EN 50363-2-1 EM2 synthetic rubber jacket for 100 m (round) to 300 m (Flat Submersible) depth
| S1RN8-F / S1RC4N8-F & S1BNH2-F — Standard Subsea & Marine Execution | Built to VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard with class 5 copper conductors (bare / tinned) and black em2 submersible elastomer sheath
| S1RN8-F / S1RC4N8-F & S1BNH2-F — Custom Drum Length & Termination Kit | Available in custom continuous subsea/wellbore drum lengths or pre-terminated assemblies
| S1RN8-F / S1RC4N8-F & S1BNH2-F — Routine & Hydrostatic Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & pressure/dimensional report

## Quality and supply
S1RN8-F / S1RC4N8-F & S1BNH2-F 0.6/1 kV 3GI3/EM2 Submersible Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/s1rn8-f-s1rc4n8-f-s1bnh2-f/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard) — DC resistance at 20 °C / optical attenuation and outer diameter within VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard) — Zero dielectric breakdown and verified insulation resistance for 0.6/1 kV rating | Every manufactured drum length
Type test | Hydrostatic pressure, water-blocking & mechanical endurance qualification (VDE 0207-20 3GI3 & EN 50363-2-1 EM2 Submersible Standard) — Verified submersion integrity, tensile load and thermal stability across −25…+80 °C | Type qualification & periodic lot audit
Standard / approval | VDE 0207-20 / EN 50363 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX S1RN8-F / S1RC4N8-F & S1BNH2-F VDE 0207-20 / EN 50363 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel subsea reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous subsea/wellbore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP