## Request a quote
Request a quotation for SANS Type 41 (640/1,100 V)
Application engineer · SANS 1520 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-41-cable-sans/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SANS 1520-1 Type 41 Flexible Mining Trailing Cable (640/1,100 V) – Dimensions & mechanical (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-41-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation 3P + 1 Pilot | Power mm² | Power Ø mm | Screen area mm² | Pilot mm² | Pilot Ø mm | Max. tension kN | Nominal OD mm | Mass ≈ kg/km
| Type 41 · 3 × 2.5 + 1 × 2.5 mm² | 2.5 | 2.1 | 8 | 2.5 | 2.1 | 0.15 | 20 | 712
| Type 41 · 3 × 4 + 1 × 4 mm² | 4 | 2.7 | 9.5 | 4 | 2.7 | 0.24 | 25 | 902
| Type 41 · 3 × 6 + 1 × 6 mm² | 6 | 3.3 | 10.4 | 6 | 3.3 | 0.36 | 26 | 1103
| Type 41 · 3 × 10 + 1 × 10 mm² | 10 | 4.2 | 19 | 10 | 4.2 | 0.6 | 29 | 1563
| Type 41 · 3 × 16 + 1 × 16 mm² | 16 | 5.3 | 22 | 16 | 5.3 | 0.95 | 33 | 2105
| Type 41 · 3 × 25 + 1 × 16 mm² | 25 | 6.8 | 25 | 16 | 5.3 | 1.1 | 39 | 2705
Each power core is individually screened with a composite tinned copper / nylon braid (0.21 mm screen wires on 2.5–6 mm²; 0.31 mm on 10–25 mm²).
Maximum tensile load applies to the three power conductors combined during reeling or trailing drag.

## Electrical & drum ampacity
SANS 1520-1 Type 41 Flexible Mining Trailing Cable (640/1,100 V) – Electrical & drum ampacity (30 °C) (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-41-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Designation Power cores | DC res. 20 °C Ω/km | DC res. 90 °C Ω/km | Reactance Ω/km | Impedance Ω/km | Laid straight A | 1 drum layer A | 2 drum layers A | 3 drum layers A | Sym. S/C (1 s) kA | Earth fault (1 s) kA
Type 41 · 3 × 2.5 mm² | 8.21 | 10.47 | 0.132 | 10.47 | 34 | 29 | 22 | 15 | 0.31 | 0.4
Type 41 · 3 × 4 mm² | 5.5 | 7.01 | 0.123 | 7.01 | 45 | 38 | 29 | 20 | 0.49 | 0.5
Type 41 · 3 × 6 mm² | 3.66 | 4.67 | 0.115 | 4.67 | 57 | 48 | 37 | 25 | 0.73 | 0.7
Type 41 · 3 × 10 mm² | 2.11 | 2.69 | 0.108 | 2.69 | 77 | 65 | 50 | 34 | 1.2 | 0.6
Type 41 · 3 × 16 mm² | 1.34 | 1.71 | 0.103 | 1.71 | 100 | 85 | 65 | 45 | 2 | 1
Type 41 · 3 × 25 mm² | 0.859 | 1.1 | 0.1 | 1.1 | 130 | 110 | 84 | 58 | 3.1 | 1.6
Current ratings based on 30 °C ambient air and 90 °C maximum conductor temperature per SANS 1520-1.
Short-circuit ratings are 1-second symmetrical phase fault and screen earth-fault capacities in kA.

## Technical data
SANS 1520-1 Type 41 Flexible Mining Trailing Cable (640/1,100 V) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-41-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 640/1,100 V (SANS 1520-1 LV mining)
Key data | Core arrangement | 3P (scr) + 1P (3 screened + 1 pilot)
Key data | Size range | 2.5–25 mm² (6 sizes · small apparatus)
Key data | Ampacity (30 °C) | 34–130 A (Laid out straight)
Key data | Operating temp. | −25 to +90 °C (EPR / twin CR rubber)
Key data | Min. bend radius | 6 × OD (Reeling & non-reeling)
Electrical | Rated voltage U0/U | 640/1,100 V AC (SANS 1520-1 Type 41 portable apparatus trailing cable)
Electrical | Current rating (30 °C) | 34 to 130 A laid out straight · drum layer derated for 1, 2 and 3 layers
Electrical | Individual phase screens | Composite tinned copper / nylon braid screen over each EPR power core (8 to 25 mm²)
Electrical | Pilot core | 1 × unscreened EPR-insulated pilot core (2.5 to 16 mm²) laid up in interstice
Thermal | Operating temperature range | −25 °C to +90 °C
Thermal | Max. conductor temperature | +90 °C continuous · +250 °C short-circuit (1 s)
Mechanical | Min. bending radius | 6 × OD
Mechanical | Max. tensile load | 0.15 kN (2.5 mm²) to 1.10 kN (25 mm²)
Mechanical | Sheath & reinforcement | CR polychloroprene inner sheath + 16-string open nylon braid + heavy-duty black CR outer sheath
Resistance | Flame & oil resistance | Flame-retardant, oil-resistant and abrasion-resistant CR polychloroprene sheath per SANS 1411-3
Resistance | Water, ozone & UV | EPR insulation and heavy-duty CR jacket resist underground mine water, ozone and surface UV
Standards | Construction standard | SANS 1520-1 · SANS 1411-1 · SANS 1411-3
Standards | Conductor class | Class 5 flexible stranded tinned annealed copper per SANS 1411-1 / IEC 60228
Identification | Outer sheath colour | Black heavy-duty polychloroprene (CR)
Identification | Type designation | SANS 1520-1 Type 41 (3 × screened power + 1 × unscreened pilot, 640/1,100 V)

## Construction
SANS 1520-1 Type 41 Flexible Mining Trailing Cable (640/1,100 V) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-41-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Power conductors (3) | Class 5 flexible stranded tinned annealed copper (2.5 to 25 mm²) | SANS 1411-1
2 | Power core insulation | Ethylene propylene rubber (EPR) thermosetting compound (640/1,100 V grade) | SANS 1411-3
3 | Individual phase screens (3) | Composite tinned copper wire and nylon textile braid over each power core (8 to 25 mm² equivalent)
4 | Pilot core (1) | Unscreened Class 5 tinned copper pilot core insulated with EPR (2.5 to 16 mm²) around rubber centre
5 | Inner sheath | Polychloroprene (CR) thermosetting elastomer inner bedding sheath | SANS 1411-3
6 | Anti-torsion reinforcement braid | Open-weave nylon reinforcement braid (minimum 16 strings) vulcanized between sheaths | SANS 1520-1
7 | Outer sheath | Heavy-duty black polychloroprene (CR) rubber outer sheath | SANS 1520-1 · SANS 1411-3
| SANS Type 41 (2.5–25 mm² · CR Sheath) | 3 screened power cores + 1 unscreened pilot core with twin CR polychloroprene sheaths for small-section trailing & reeling
| Step-Up Option: SANS Type 61A / 61B (35–150 mm²) | For larger 640/1,100 V continuous miners and shuttle cars above 25 mm², specify SANS Type 61A (TPU) or Type 61B (CR)

## Quality and supply
SANS 1520-1 Type 41 Flexible Mining Trailing Cable (640/1,100 V) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-41-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage dielectric test & spark test — Routine AC voltage withstand test on 640/1,100 V EPR cores per SANS 1520-1 | Every shipping drum
Routine test | Conductor, screen & pilot DC resistance — Verified on all 3 power conductors, 3 individual copper/nylon screens and pilot core per SANS 1411-1 | Every shipping drum
Sample test | CR sheath oil, flame & mechanical tests — Polychloroprene compound tested to SANS 1411-3 and SANS 1520-1 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · SANS 1520-1 · TYPE 41 · 640/1100V · 3 x [mm²] + P
Supply | Delivery form: Export seaworthy fumigated wooden drums matched to 6 × OD bend radius
Supply | Lengths: Standard drum lengths or custom cut lengths per mine gate-end schedule
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None