## Request a quote
Request a quotation for SANS Type 611 / 611-ECC (6.35/11 kV)
Application engineer · SANS 1520 medium-voltage mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-611-cable-sans/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SANS 1520-2 Type 611 / 611-ECC 6.35/11 kV Mining Cable – Dimensions · Type 611 & 611-ECC (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-611-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation Power cores | Power mm² | Power Ø mm | Screen mm² | Pilot mm² | ECC size mm² (-ECC) | Max. tension kN | Nominal OD mm | Mass (Std) kg/100m | Mass (Type 611) kg/km | Mass (611-ECC) kg/km
| Type 611 / 611-ECC · 3 × 25 mm² | 25 | 6.8 | 29 | 10 | 16 | 1.1 | 50.7 | 410 | 4100 | 4200
| Type 611 / 611-ECC · 3 × 35 mm² | 35 | 8.5 | 31 | 10 | 25 | 1.6 | 52.2 | 450 | 4500 | 4600
| Type 611 / 611-ECC · 3 × 50 mm² | 50 | 10.3 | 34 | 10 | 25 | 2.3 | 59.4 | 530 | 5300 | 5400
| Type 611 / 611-ECC · 3 × 70 mm² | 70 | 11.9 | 37 | 16 | 35 | 3.2 | 60.4 | 650 | 6500 | 6700
| Type 611 / 611-ECC · 3 × 95 mm² | 95 | 13.5 | 41 | 16 | 50 | 4.3 | 65.2 | 800 | 8000 | 8200
| Type 611 / 611-ECC · 3 × 120 mm² | 120 | 15.5 | 43 | 16 | 70 | 5.4 | 71.3 | 980 | 9800 | 10200
| Type 611 / 611-ECC · 3 × 150 mm² | 150 | 17.3 | 46 | 25 | 95 | 6.8 | 75 | 1070 | 10700 | 10900
| Type 611 / 611-ECC · 3 × 185 mm² | 185 | 20.2 | 49 | 25 | 95 | 8.3 | 85.1 | 1340 | 13400 | 13900
| Type 611 / 611-ECC · 3 × 240 mm² | 240 | 22.9 | 52 | 25 | 120 | 10.8 | 85.6 | 1470 | 14700 | 15000
Type 611 incorporates 3 EPM-insulated pilot cores; Type 611-ECC replaces one pilot core with a tinned copper earth-continuity conductor (ECC) of the size shown.
Both variants share the same nominal overall diameter (OD) and maximum tensile load.

## Electrical & 1s fault ratings
SANS 1520-2 Type 611 / 611-ECC 6.35/11 kV Mining Cable – Electrical & 1s fault ratings (30 °C) (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-611-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Designation Power cores | DC res. 20 °C Ω/km | DC res. 90 °C Ω/km | Reactance Ω/km | Impedance 90 °C Ω/km | Screen res. Ω/km | ECC res. Ω/km | Current (30 °C) A | Phase S/C (1 s) kA | Earth S/C (Std) kA (1 s) | Earth S/C (-ECC) kA (1 s)
Type 611 / 611-ECC · 3 × 25 mm² | 0.795 | 1.05 | 0.134 | 1.06 | 1.6 | 0.7 | 105 | 3.1 | 1.6 | 3.6
Type 611 / 611-ECC · 3 × 35 mm² | 0.565 | 0.749 | 0.124 | 0.759 | 1.2 | 0.5 | 130 | 4.3 | 2.1 | 5
Type 611 / 611-ECC · 3 × 50 mm² | 0.393 | 0.521 | 0.117 | 0.534 | 0.8 | 0.5 | 160 | 6.1 | 3.1 | 5
Type 611 / 611-ECC · 3 × 70 mm² | 0.277 | 0.368 | 0.113 | 0.385 | 0.7 | 0.4 | 195 | 8.5 | 3.5 | 7.5
Type 611 / 611-ECC · 3 × 95 mm² | 0.21 | 0.279 | 0.108 | 0.299 | 0.6 | 0.3 | 230 | 11.6 | 4.1 | 9
Type 611 / 611-ECC · 3 × 120 mm² | 0.164 | 0.218 | 0.103 | 0.241 | 0.6 | 0.23 | 260 | 14.6 | 4.1 | 11.5
Type 611 / 611-ECC · 3 × 150 mm² | 0.132 | 0.176 | 0.098 | 0.201 | 0.6 | 0.18 | 300 | 18.3 | 4.1 | 14
Type 611 / 611-ECC · 3 × 185 mm² | 0.108 | 0.145 | 0.096 | 0.174 | 0.6 | 0.18 | 340 | 22.57 | 4.1 | 14
Type 611 / 611-ECC · 3 × 240 mm² | 0.0817 | 0.11 | 0.092 | 0.143 | 0.6 | 0.15 | 400 | 29.3 | 4.1 | 17
Current ratings are based on 30 °C ambient temperature and 90 °C maximum conductor temperature.
Adding the ECC conductor in Type 611-ECC increases the 1-second earth-fault withstand from 1.6 to 4.1 kA (screens only) to 3.6 to 17.0 kA (screens + ECC).

## Technical data
SANS 1520-2 Type 611 / 611-ECC 6.35/11 kV Mining Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-611-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 6.35/11 kV (SANS 1520-2 MV mining)
Key data | Core arrangement | 3P + 3P / ECC (Type 611 or 611-ECC)
Key data | Size range | 25–240 mm² (9 standard sizes)
Key data | Ampacity (30 °C) | 105–400 A (Laid out straight)
Key data | Operating temp. | −25 to +90 °C (EPR / twin CR rubber)
Key data | Min. bend radius | 9 × OD (Reeling & trailing duty)
Electrical | Rated voltage U0/U | 6.35/11 kV AC (SANS 1520-2 Type 611 and Type 611-ECC)
Electrical | Current rating (30 °C) | 105–400 A at 30 °C ambient air and 90 °C conductor temperature
Electrical | Phase screening & stress control | Triple-extruded EPR with strippable semi-conducting core screen + composite tinned copper / nylon braid (29–52 mm²)
Electrical | Pilot & ECC variants | Type 611: 3 × EPM-insulated pilots · Type 611-ECC: 2 × pilots + 1 × bare tinned copper ECC (16 to 120 mm²)
Thermal | Operating temperature range | −25 °C to +90 °C
Thermal | Short-circuit & earth-fault rating (1 s) | Phase S/C: 3.1–29.3 kA (1 s) · Earth fault: 1.6–4.1 kA (Type 611 screens) or 3.6–17.0 kA (Type 611-ECC)
Mechanical | Min. bending radius | 9 × OD (reeling, dragline trailing and section-feeder service)
Mechanical | Max. tensile load | 1.1 to 10.8 kN
Mechanical | Twin CR sheaths & reinforcement | CR polychloroprene inner sheath + 16-string open nylon braid + black CR polychloroprene outer sheath
Resistance | UV, sunlight & oil resistance | UV resistant, sunlight resistant, oil resistant and flame retardant per SANS 1520-2 / SANS 1411-3
Resistance | Open-cast & underground abrasion | Heavy-duty polychloroprene (CR) twin sheath resists pit-bench rock drag, shovel reeling and moisture
Standards | Construction standard | SANS 1520-2 · SANS 1411-1 · SANS 1411-3
Standards | Conductor class | Class 5 flexible stranded tinned annealed copper per SANS 1411-1
Identification | Outer sheath colour | Black polychloroprene (CR)
Identification | Type designation | SANS 1520-2 Type 611 (3 pilots) & Type 611-ECC (2 pilots + 1 ECC), 6.35/11 kV

## Construction
SANS 1520-2 Type 611 / 611-ECC 6.35/11 kV Mining Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-611-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Power conductors (3) | Class 5 flexible stranded tinned annealed copper (25–240 mm²) | SANS 1411-1
2 | Power core insulation | Triple-extruded EPR thermosetting compound with strippable semi-conducting core screen (6.35/11 kV grade) | SANS 1411-3 · SANS 1520-2
3 | Individual phase screens (3) | Composite tinned copper (0.31 mm wires) and nylon textile braid over each power core | 1.6–4.1 kA 1s screen fault
4 | Pilots (3) or 2 Pilots + ECC (611-ECC) | Three EPM-insulated pilot cores (10 to 25 mm²), or one pilot replaced by a tinned copper ECC (16 to 120 mm²) | Up to 17 kA 1s earth fault
5 | Inner sheath | Polychloroprene (CR) thermosetting elastomer inner sheath | SANS 1411-3
6 | Reinforcement braid | Open-weave nylon reinforcement braid (minimum 16 strings) | SANS 1520-2
7 | Outer sheath | Black UV-, sunlight- and oil-resistant polychloroprene (CR) rubber outer sheath | SANS 1520-2 · SANS 1411-3
| SANS Type 611 (3 Insulated EPM Pilot Cores) | 3 individually screened 6.35/11 kV power cores + 3 EPM-insulated interstitial pilot cores (10 to 25 mm²)
| SANS Type 611-ECC (2 Pilots + 1 Tinned Copper ECC) | Replaces one pilot core with a 16 to 120 mm² tinned copper earth-continuity conductor to raise 1s earth-fault capacity to 3.6 to 17.0 kA

## Quality and supply
SANS 1520-2 Type 611 / 611-ECC 6.35/11 kV Mining Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-611-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Medium-voltage AC withstand & partial-discharge test — Routine AC high-voltage and partial-discharge test on 6.35/11 kV EPR cores per SANS 1520-2 | Every shipping drum
Routine test | Conductor, screen & ECC DC resistance test — Verified against maximum conductor resistance and minimum screen / ECC resistance limits | Every shipping drum
Sample test | CR sheath UV, oil, flame & mechanical test — Inner and outer polychloroprene sheaths tested to SANS 1411-3 and SANS 1520-2 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · SANS 1520-2 · TYPE 611 / 611-ECC · 6.35/11kV · 3 x [mm²] · EPR/CR
Supply | Delivery form: Export seaworthy wooden or steel drums matched to 9 × OD minimum bend radius
Supply | Variants: Available in standard Type 611 (3 pilots) or Type 611-ECC (2 pilots + 1 tinned copper ECC)
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None