## Request a quote
Request a quotation for SANS Type 61A (640/1,100 V)
Application engineer · SANS 1520 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-61a-cable-sans/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SANS 1520-1 Type 61A TPU Mining Trailing Cable (640/1,100 V) – Sizes, dimensions & ratings (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-61a-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation 3P + 1 Pilot | Power mm² | Power Ø mm | Screen area mm² | Pilot mm² | Pilot Ø mm | Max. tension kN | Nominal OD mm | Mass ≈ kg/km | Current (30 °C) A | Sym. S/C (1 s) kA
| Type 61A · 3 × 25 + 1 × 10 mm² | 25 | 6.8 | 25 | 10 | 4.2 | 1.1 | 40.5 | 2850 | 130 | 3.1
| Type 61A · 3 × 35 + 1 × 10 mm² | 35 | 8.5 | 27 | 10 | 4.2 | 1.6 | 43.5 | 3320 | 160 | 4.3
| Type 61A · 3 × 50 + 1 × 10 mm² | 50 | 10.3 | 32 | 10 | 4.2 | 2.3 | 47 | 4050 | 200 | 6.1
| Type 61A · 3 × 70 + 1 × 16 mm² | 70 | 11.9 | 37 | 16 | 5.3 | 3.2 | 53 | 5120 | 245 | 8.5
| Type 61A · 3 × 95 + 1 × 16 mm² | 95 | 13.5 | 43 | 16 | 5.3 | 4.3 | 59.1 | 6340 | 295 | 11.6
| Type 61A · 3 × 120 + 1 × 16 mm² | 120 | 15.5 | 47 | 16 | 5.3 | 5.4 | 63 | 7450 | 345 | 14.6
| Type 61A · 3 × 150 + 1 × 25 mm² | 150 | 17.3 | 52 | 25 | 6.8 | 6.8 | 67.5 | 8750 | 390 | 18.3
95 mm² row (59.1 mm OD, 6,340 kg/km, 4.3 kN max tension, 43 mm² screen, 16 mm² pilot) is directly from the TEBAOFLEX Type 61A datasheet; companion SANS 1520-1 sizes (25–150 mm²) are typical SANS 1520-1 values.
Available with black TPU outer sheath or transparent TPU over orange/silver reflective tape.

## Technical data
SANS 1520-1 Type 61A TPU Mining Trailing Cable (640/1,100 V) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-61a-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 640/1,100 V (SANS 1520-1 LV mining)
Key data | Core arrangement | 3P (scr) + 1P (3 screened + 1 pilot)
Key data | Size range | 25–150 mm² (95 mm² reference + series)
Key data | Outer sheath | TPU + CR inner (Black or reflective TPU)
Key data | Operating temp. | −25 to +90 °C (EPR / CR + TPU)
Key data | Min. bend radius | 6 × OD (Reeling & non-reeling)
Electrical | Rated voltage U0/U | 640/1,100 V AC (SANS 1520-1 Type 61A heavy-duty trailing & reeling cable)
Electrical | Current rating (30 °C) | 130 to 390 A laid out straight (295 A for 95 mm² reference size)
Electrical | Individual phase screens | Composite tinned copper / nylon braid screen over each EPR power core (0.31 mm wires, 43 mm² on 95 mm²)
Electrical | Pilot core | 1 × unscreened EPR-insulated pilot core (10 to 25 mm²; 16 mm² on 95 mm²) laid up in interstice
Thermal | Operating temperature range | −25 °C to +90 °C
Thermal | Max. conductor temperature | +90 °C continuous · +250 °C short-circuit (1 s)
Mechanical | Min. bending radius | 6 × OD (reeling and non-reeling mobile mining duty)
Mechanical | Outer & inner sheath system | CR polychloroprene inner sheath + 16-string open nylon braid + TPU thermoplastic polyurethane outer sheath
Mechanical | High-visibility reflective option | Black TPU or transparent TPU over orange/silver reflective tape for dark underground headings
Resistance | Cut, tear & rock abrasion | TPU outer sheath provides superior tear, rock-cut and shuttle-car run-over resistance vs standard CR
Resistance | UV, ozone & oil resistance | UV resistant, ozone resistant, sunlight resistant and oil resistant
Standards | Construction standard | SANS 1520-1 · SANS 1411-1 · SANS 1411-3 · ICEA S-75-381 Tab. 3-3
Standards | Conductor class | Class 5 flexible stranded tinned annealed copper per SANS 1411-1
Identification | Outer sheath colour | Black TPU or transparent TPU with orange/silver reflective tape underneath
Identification | Type designation | SANS 1520-1 Type 61A (3 × screened power + 1 × unscreened pilot, TPU outer sheath)

## Construction
SANS 1520-1 Type 61A TPU Mining Trailing Cable (640/1,100 V) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-61a-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Power conductors (3) | Class 5 flexible stranded tinned annealed copper per SANS 1411-1 | SANS 1411-1
2 | Power core insulation | Ethylene propylene rubber (EPR) thermosetting compound (640/1,100 V grade) | SANS 1411-3
3 | Individual phase screens (3) | Composite tinned copper (0.31 mm wires) and nylon braid screen over each power core
4 | Pilot core (1) | Unscreened Class 5 tinned copper pilot core with EPR insulation laid up in interstice
5 | Inner sheath | Polychloroprene (CR) rubber inner sheath | SANS 1411-3
6 | Reinforcement braid | Open-weave nylon reinforcement braid (minimum 16 strings) | SANS 1520-1
7 | Outer sheath (TPU) | Thermoplastic polyurethane (TPU), black or transparent over orange/silver reflective tape | SANS 1520-1 · ICEA S-75-381 Tab. 3-3
| Black Heavy-Duty TPU Outer Sheath | Standard black thermoplastic polyurethane outer sheath over CR inner sheath and 16-string nylon braid
| Transparent TPU + Orange/Silver Reflective Tape | Transparent TPU outer sheath encapsulating a helically wound orange/silver retro-reflective tape for underground visibility

## Quality and supply
SANS 1520-1 Type 61A TPU Mining Trailing Cable (640/1,100 V) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-61a-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage dielectric withstand test — Routine AC withstand test on 640/1,100 V EPR cores per SANS 1520-1 | Every shipping drum
Routine test | Conductor, screen & pilot DC resistance — Verified on all 3 power conductors, 3 individual copper/nylon screens and pilot core | Every shipping drum
Sample test | TPU outer sheath tear, abrasion & UV/oil test — Tested to SANS 1520-1, SANS 1411-3 and ICEA S-75-381 Tab. 3-3 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · SANS 1520-1 · TYPE 61A · 640/1100V · 3 x [mm²] + P · EPR/CR/TPU
Supply | Delivery form: Export seaworthy wooden drums matched to 6 × OD bend radius
Supply | Sheath options: Black TPU standard, or transparent TPU over orange/silver reflective tape
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None