## Request a quote
Request a quotation for SANS Type 61B (0.64/1.1 kV)
Application engineer · SANS 1520 mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-61b-cable-sans/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SANS 1520-1 Type 61B Copper-Screened Mining Cable (0.64/1.1 kV) – Physical & mechanical properties (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-61b-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation 3P + 3 Pilots | Power mm² | Power Ø mm | Screen (80 %) mm² | Pilots (3) mm² | Pilot Ø mm | Cable OD mm | Mass kg/m | Mass ≈ kg/km | Min. bend R mm | Max. tension kN
| Type 61B · 3 × 35 + 3 × 6 mm² | 35 | 8.5 | 27 | 6 | 3.2 | 41 | 3.1 | 3100 | 300 | 1.6
| Type 61B · 3 × 50 + 3 × 6 mm² | 50 | 10.3 | 32 | 6 | 3.2 | 42.5 | 3.6 | 3600 | 340 | 2.3
| Type 61B · 3 × 70 + 3 × 16 mm² | 70 | 11.9 | 37 | 16 | 5.2 | 48 | 4.8 | 4800 | 390 | 3.2
| Type 61B · 3 × 95 + 3 × 16 mm² | 95 | 13.5 | 43 | 16 | 5.2 | 52.3 | 5.7 | 5700 | 430 | 4.3
| Type 61B · 3 × 120 + 3 × 16 mm² | 120 | 15.5 | 47 | 16 | 5.2 | 58 | 7.1 | 7100 | 460 | 5.4
| Type 61B · 3 × 150 + 3 × 16 mm² | 150 | 17.3 | 52 | 16 | 5.2 | 63.5 | 8.5 | 8500 | 500 | 6.8
All sizes use an 80 % fill tinned copper wire braid screen (0.31 mm wires) and a right-hand core lay ratio of 12 × pitch circle diameter (PCD).
Three unscreened pilot cores (one in each outer interstice) are laid up around a semi-conductive rubber centre.

## Electrical & short-circuit
SANS 1520-1 Type 61B Copper-Screened Mining Cable (0.64/1.1 kV) – Electrical & short-circuit (30 °C) (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-61b-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Designation Power cores | DC res. 20 °C Ω/km | DC res. 90 °C Ω/km | Reactance Ω/km | Impedance 90 °C Ω/km | Laid straight A (30 °C) | Sym. S/C (1 s) kA | Earth fault (1 s) kA
Type 61B · 3 × 35 mm² | 0.576 | 0.734 | 0.09 | 0.74 | 160 | 4.3 | 2.1
Type 61B · 3 × 50 mm² | 0.401 | 0.511 | 0.09 | 0.519 | 200 | 6.1 | 3.1
Type 61B · 3 × 70 mm² | 0.283 | 0.36 | 0.088 | 0.371 | 245 | 8.5 | 3.5
Type 61B · 3 × 95 mm² | 0.214 | 0.273 | 0.086 | 0.287 | 295 | 11.6 | 4.1
Type 61B · 3 × 120 mm² | 0.167 | 0.213 | 0.086 | 0.23 | 345 | 14.6 | 4.1
Type 61B · 3 × 150 mm² | 0.135 | 0.171 | 0.085 | 0.191 | 390 | 18.3 | 4.1
Current rating applies to cable laid out straight at 30 °C ambient temperature.
Earth-fault short-circuit capacity (2.1 to 4.1 kA for 1 second) is carried by the three 80 % fill tinned copper braid screens.

## Technical data
SANS 1520-1 Type 61B Copper-Screened Mining Cable (0.64/1.1 kV) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-61b-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.64/1.1 kV (SANS 1520-1 LV mining)
Key data | Core arrangement | 3P (scr) + 3P (3 screened + 3 pilots)
Key data | Size range | 35–150 mm² (6 sizes · 35 to 150 mm²)
Key data | Ampacity (30 °C) | 160–390 A (Laid out straight)
Key data | Operating temp. | −25 to +90 °C (RD 3 EPR / RS 6 CR)
Key data | Min. bend radius | 300–500 mm (Approx. 7.3–8 × OD)
Electrical | Rated voltage U0/U | 0.64/1.1 kV (640/1,100 V AC per SANS 1520-1 Type 61B)
Electrical | Current rating (30 °C) | 160 to 390 A laid out straight at 30 °C ambient
Electrical | Triple-extruded EPR & copper screens | Semi-conducting conductor screen + Type RD 3 EPR + strippable core screen + tinned copper braid (80 % fill, 27–52 mm²)
Electrical | Three interstitial pilot cores | 3 × unscreened pilot cores (6 mm² on 35–50 mm²; 16 mm² on 70–150 mm²), one in each interstice
Thermal | Operating temperature range | −25 °C to +90 °C
Thermal | Short-circuit & earth-fault rating (1 s) | Symmetrical phase S/C: 4.3 to 18.3 kA (1 s) · Earth-fault screen rating: 2.1 to 4.1 kA (1 s)
Mechanical | Min. bending radius | 300 mm (35 mm²) to 500 mm (150 mm²) — approx. 7.3 to 8 × OD
Mechanical | Max. tensile load | 1.6 kN (35 mm²) to 6.8 kN (150 mm²)
Mechanical | Twin RS 6 polychloroprene sheaths | Type RS 6 polychloroprene inner sheath + 16-string open nylon braid + black Type RS 6 polychloroprene outer sheath
Resistance | Flame, oil & water resistance | Flame retardant, oil resistant and water resistant per SANS 1411-3 Type RS 6
Resistance | UV, sunlight & ozone | UV, sunlight and ozone resistant for surface and underground hazardous-area mining
Standards | Construction standard | SANS 1520-1 · SANS 1411-1 · SANS 1411-3
Standards | Compounds | Insulation: EPR Type RD 3 · Inner & outer sheaths: Polychloroprene Type RS 6 (SANS 1411-3)
Identification | Outer sheath colour | Black Type RS 6 polychloroprene
Identification | Type designation | SANS 1520-1 Type 61B (3 × copper-screened power + 3 × unscreened pilots, non-reeling)

## Construction
SANS 1520-1 Type 61B Copper-Screened Mining Cable (0.64/1.1 kV) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-61b-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Power conductors (3) | Class 5 flexible stranded tinned annealed copper (35 to 150 mm²) | SANS 1411-1
2 | Triple-extruded RD 3 EPR | Semi-conducting rubber conductor screen + EPR Type RD 3 insulation + strippable semi-conducting core screen | SANS 1411-3 Type RD 3
3 | Tinned copper braid screens (3) | Individual tinned copper wire braid screen (0.31 mm wires, 80 % fill, 27 to 52 mm² cross-section) | 2.1–4.1 kA 1s earth fault
4 | Interstitial pilot cores (3) | Three unscreened flexible tinned copper pilot cores (3 × 6 mm² or 3 × 16 mm²), one in each interstice around semi-conductive rubber centre
5 | Inner sheath | Polychloroprene thermosetting compound Type RS 6 | SANS 1411-3 Type RS 6
6 | Reinforcement braid | Open-weave nylon reinforcement braid (minimum 16 nylon strings) | SANS 1520-1
7 | Outer sheath | Black polychloroprene thermosetting compound Type RS 6 | SANS 1520-1 · SANS 1411-3
| SANS Type 61B (35–50 mm² · 3 × 6 mm² Pilots) | 3 copper-screened power cores + 3 × 6 mm² unscreened interstitial pilot cores around a semi-conductive rubber centre
| SANS Type 61B (70–150 mm² · 3 × 16 mm² Pilots) | 3 copper-screened power cores + 3 × 16 mm² unscreened interstitial pilot cores for high-current movable mining equipment

## Quality and supply
SANS 1520-1 Type 61B Copper-Screened Mining Cable (0.64/1.1 kV) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-61b-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-1 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC high-voltage & partial-discharge / screen test — Routine AC withstand test on triple-extruded Type RD 3 EPR cores per SANS 1520-1 | Every shipping drum
Routine test | Power & pilot DC resistance + screen continuity — Verified on all 3 power cores, 3 tinned copper braid screens and 3 interstitial pilots | Every shipping drum
Sample test | Type RS 6 polychloroprene flame, oil & mechanical tests — Tested to SANS 1411-3 Type RS 6 and SANS 1520-1 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · SANS 1520-1 · TYPE 61B · 0.64/1.1KV · 3 x [mm²] + 3P · RD3/RS6
Supply | Delivery form: Export seaworthy wooden drums matched to minimum bend radius (300–500 mm)
Supply | Lengths: Standard or custom cut lengths per underground section schedule
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None