## Request a quote
Request a quotation for SANS Type 63 (1.9/3.3 kV)
Application engineer · SANS 1520 medium-voltage mining cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/type-63-cable-sans/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SANS 1520-2 Type 63 1.9/3.3 kV Flexible Trailing Mining Cable – Dimensions & mechanical (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-63-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation 3P + 1 Pilot | Power mm² | Power Ø mm | Screen area mm² | Pilot mm² | Pilot Ø mm | Max. tension kN | Nominal OD mm | Mass kg/100m | Mass ≈ kg/km
| Type 63 · 3 × 25 + 1 × 10 mm² | 25 | 6.8 | 31 | 10 | 4.2 | 1.1 | 44 | 360 | 3600
| Type 63 · 3 × 35 + 1 × 10 mm² | 35 | 8.5 | 33 | 10 | 4.2 | 1.6 | 48 | 420 | 4200
| Type 63 · 3 × 50 + 1 × 10 mm² | 50 | 10.3 | 38 | 10 | 5.3 | 2.3 | 50.5 | 510 | 5100
| Type 63 · 3 × 70 + 1 × 16 mm² | 70 | 11.9 | 42 | 16 | 5.3 | 3.2 | 56 | 640 | 6400
| Type 63 · 3 × 95 + 1 × 16 mm² | 95 | 13.5 | 47 | 16 | 5.3 | 4.3 | 61 | 770 | 7700
| Type 63 · 3 × 120 + 1 × 16 mm² | 120 | 15.5 | 50 | 16 | 5.3 | 5.4 | 63 | 850 | 8500
| Type 63 · 3 × 150 + 1 × 25 mm² | 150 | 17.3 | 55 | 25 | 6.8 | 6.8 | 66 | 1050 | 10500
| Type 63 · 3 × 185 + 1 × 25 mm² | 185 | 20.2 | 60 | 25 | 6.8 | 8.3 | 72 | 1140 | 11400
| Type 63 · 3 × 240 + 1 × 25 mm² | 240 | 22.9 | 64 | 25 | 6.8 | 10.8 | 78 | 1400 | 14000
Each power core is individually screened with a composite 0.31 mm tinned copper / nylon braid (31 to 64 mm² total metallic screen area).
Cable mass is shown in both kg/100 m (South African catalogue convention) and kg/km.

## Electrical & short-circuit
SANS 1520-2 Type 63 1.9/3.3 kV Flexible Trailing Mining Cable – Electrical & short-circuit (30 °C) (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-63-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Designation Power cores | DC res. 20 °C Ω/km | DC res. 90 °C Ω/km | Reactance Ω/km | Impedance 90 °C Ω/km | Laid straight A (30 °C) | Sym. S/C (1 s) kA | Earth fault (1 s) kA
Type 63 · 3 × 25 mm² | 0.859 | 1.1 | 0.122 | 1.11 | 130 | 3.1 | 1.6
Type 63 · 3 × 35 mm² | 0.61 | 0.778 | 0.113 | 0.786 | 160 | 4.3 | 2.1
Type 63 · 3 × 50 mm² | 0.424 | 0.542 | 0.107 | 0.552 | 200 | 6.1 | 3.1
Type 63 · 3 × 70 mm² | 0.299 | 0.382 | 0.103 | 0.396 | 245 | 8.5 | 3.5
Type 63 · 3 × 95 mm² | 0.227 | 0.29 | 0.09 | 0.304 | 295 | 11.6 | 4.1
Type 63 · 3 × 120 mm² | 0.177 | 0.227 | 0.088 | 0.243 | 345 | 14.6 | 4.1
Type 63 · 3 × 150 mm² | 0.143 | 0.183 | 0.085 | 0.202 | 390 | 18.3 | 4.1
Type 63 · 3 × 185 mm² | 0.117 | 0.15 | 0.084 | 0.172 | 440 | 23 | 4.1
Type 63 · 3 × 240 mm² | 0.0882 | 0.115 | 0.083 | 0.142 | 520 | 29 | 4.1
Current rating applies to cable laid out straight in free air at 30 °C ambient temperature.
Short-circuit values are 1-second symmetrical phase fault and screen earth-fault capacities in kA.

## Technical data
SANS 1520-2 Type 63 1.9/3.3 kV Flexible Trailing Mining Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-63-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.9/3.3 kV (SANS 1520-2 MV mining)
Key data | Core arrangement | 3P (scr) + 1P (3 screened + 1 pilot)
Key data | Size range | 25–240 mm² (9 sizes · 25 to 240 mm²)
Key data | Ampacity (30 °C) | 130–520 A (Laid out straight)
Key data | Operating temp. | −25 to +90 °C (EPR / twin CR rubber)
Key data | Min. bend radius | 6 × OD (Reeling & non-reeling)
Electrical | Rated voltage U0/U | 1.9/3.3 kV AC (SANS 1520-2 Type 63 medium-voltage trailing & reeling cable)
Electrical | Current rating (30 °C) | 130 to 520 A laid out straight at 30 °C ambient
Electrical | Individual phase screens | Composite tinned copper / nylon braid screen over each EPR power core (0.31 mm wires, 31 to 64 mm²)
Electrical | Pilot core | 1 × unscreened EPR-insulated pilot core (10, 16 or 25 mm²) laid up with power cores
Thermal | Operating temperature range | −25 °C to +90 °C
Thermal | Short-circuit & earth-fault rating (1 s) | Symmetrical phase S/C: 3.1 to 29.0 kA (1 s) · Earth-fault screen rating: 1.6 to 4.1 kA (1 s)
Mechanical | Min. bending radius | 6 × OD (reeling and non-reeling service)
Mechanical | Max. tensile load | 1.1 kN (25 mm²) to 10.8 kN (240 mm²)
Mechanical | Twin CR sheaths & reinforcement | CR polychloroprene inner sheath + 16-string open nylon braid + black CR polychloroprene outer sheath
Resistance | Flame, oil & abrasion | Heavy-duty polychloroprene (CR) outer sheath resists flame, mineral oil, rock cuts and coal-face drag
Resistance | Water, ozone & UV | EPR insulation and twin CR sheaths withstand wet underground headings and open-cast UV exposure
Standards | Construction standard | SANS 1520-2 · SANS 1411-1 · SANS 1411-3
Standards | Conductor class | Class 5 flexible stranded tinned annealed copper per SANS 1411-1
Identification | Outer sheath colour | Black polychloroprene (CR)
Identification | Type designation | SANS 1520-2 Type 63 (3 × screened power + 1 × unscreened pilot, 1.9/3.3 kV)

## Construction
SANS 1520-2 Type 63 1.9/3.3 kV Flexible Trailing Mining Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-63-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Power conductors (3) | Class 5 flexible stranded tinned annealed copper (25 to 240 mm²) | SANS 1411-1
2 | Power core insulation | Ethylene propylene rubber (EPR) thermosetting compound (1.9/3.3 kV wall) | SANS 1411-3
3 | Individual phase screens (3) | Composite tinned copper (0.31 mm wires) and nylon textile braid over each power core (31 to 64 mm²) | 1.6–4.1 kA 1s earth fault
4 | Pilot core (1) | Unscreened Class 5 tinned copper pilot core insulated with EPR (10, 16 or 25 mm²) around rubber centre
5 | Inner sheath | Polychloroprene (CR) rubber inner bedding sheath | SANS 1411-3
6 | Reinforcement braid | Open-weave nylon reinforcement braid (minimum 16 strings) | SANS 1520-2
7 | Outer sheath | Heavy-duty black polychloroprene (CR) rubber outer sheath | SANS 1520-2 · SANS 1411-3
| SANS Type 63 (25–50 mm² · 10 mm² Pilot) | 3 screened 1.9/3.3 kV power cores + 1 × 10 mm² unscreened pilot core for drills, pumps and auxiliary 3.3 kV drives
| SANS Type 63 (70–240 mm² · 16 or 25 mm² Pilot) | 3 screened 1.9/3.3 kV power cores + 1 × 16 mm² (70–120 mm²) or 25 mm² (150–240 mm²) pilot for continuous miners and shearers

## Quality and supply
SANS 1520-2 Type 63 1.9/3.3 kV Flexible Trailing Mining Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/type-63-cable-sans/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on SANS 1520-2 · SANS 1411-1 & -3. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Medium-voltage AC withstand & partial-discharge test — Routine AC dielectric withstand test on 1.9/3.3 kV EPR power cores per SANS 1520-2 | Every shipping drum
Routine test | Power, screen & pilot DC resistance — Verified on all 3 power conductors, 3 individual copper/nylon screens and pilot core | Every shipping drum
Sample test | CR sheath flame, oil & mechanical test — Polychloroprene inner and outer sheaths tested to SANS 1411-3 and SANS 1520-2 | Production batch
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · SANS 1520-2 · TYPE 63 · 1.9/3.3KV · 3 x [mm²] + P · EPR/CR
Supply | Delivery form: Export seaworthy wooden drums matched to 6 × OD minimum bend radius
Supply | Lengths: Standard or custom cut lengths per 3.3 kV mining section schedule
Supply | Certificate: EN 10204 3.1 factory routine test certificate with every drum
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None