## Request a quote
Request a quotation for SCGMS 19050 Type 1A / 1B
Application engineer · mining & tunnelling cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/scgms-19050-type-1a-1b-unscreened-mining-feeder-auxiliary-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SCGMS 19050 Type 1A / 1B Unscreened Mining Feeder & Auxiliary – Dimensions, weights & free-air ampacity (11)
TEBAOFLEX ¦ https://tebaoflex.com/cables/scgms-19050-type-1a-1b-unscreened-mining-feeder-auxiliary-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on Charbonnages de France SCGMS 19050 / NF M 82-375 / IEC 60245. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Voltage | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | In air 30 °C A | Min. bend R mm | Series
| SCGMS 19050 Type 1A 4G4 | 4G4 mm² | 0.6/1 kV | 16.2 | 154 | 375 | 36 | 97 | SCGMS 19050 Type 1A — 0.6/1 kV Unscreened Flexible Mining Power Feeders
| SCGMS 19050 Type 1A 4G10 | 4G10 mm² | 0.6/1 kV | 21.8 | 384 | 720 | 63 | 131 | SCGMS 19050 Type 1A — 0.6/1 kV Unscreened Flexible Mining Power Feeders
| SCGMS 19050 Type 1A 4G16 | 4G16 mm² | 0.6/1 kV | 25 | 614 | 1020 | 84 | 150 | SCGMS 19050 Type 1A — 0.6/1 kV Unscreened Flexible Mining Power Feeders
| SCGMS 19050 Type 1A 4G25 | 4G25 mm² | 0.6/1 kV | 29.5 | 960 | 1490 | 112 | 177 | SCGMS 19050 Type 1A — 0.6/1 kV Unscreened Flexible Mining Power Feeders
| SCGMS 19050 Type 1A 4G35 | 4G35 mm² | 0.6/1 kV | 32.8 | 1344 | 1940 | 138 | 197 | SCGMS 19050 Type 1A — 0.6/1 kV Unscreened Flexible Mining Power Feeders
| SCGMS 19050 Type 1A 4G50 | 4G50 mm² | 0.6/1 kV | 37.6 | 1920 | 2650 | 168 | 226 | SCGMS 19050 Type 1A — 0.6/1 kV Unscreened Flexible Mining Power Feeders
| SCGMS 19050 Type 1A 4G70 | 4G70 mm² | 0.6/1 kV | 42.5 | 2688 | 3580 | 213 | 255 | SCGMS 19050 Type 1A — 0.6/1 kV Unscreened Flexible Mining Power Feeders
| SCGMS 19050 Type 1A 4G95 | 4G95 mm² | 0.6/1 kV | 47.8 | 3648 | 4690 | 258 | 287 | SCGMS 19050 Type 1A — 0.6/1 kV Unscreened Flexible Mining Power Feeders
| SCGMS 19050 Type 1B 7G1.5 | 7G1.5 mm² | 0.6/1 kV | 15.8 | 101 | 330 | 16 | 95 | SCGMS 19050 Type 1B — 0.6/1 kV Unscreened Auxiliary Control & Signalling Cables
| SCGMS 19050 Type 1B 12G2.5 | 12G2.5 mm² | 0.6/1 kV | 22.4 | 288 | 710 | 18 | 134 | SCGMS 19050 Type 1B — 0.6/1 kV Unscreened Auxiliary Control & Signalling Cables
| SCGMS 19050 Type 1B 19G1.5 | 19G1.5 mm² | 0.6/1 kV | 23 | 274 | 745 | 12 | 138 | SCGMS 19050 Type 1B — 0.6/1 kV Unscreened Auxiliary Control & Signalling Cables
Single-core and 3-core / 5-core Type 1A sizes up to 150 mm² are also manufactured.

## Technical data
SCGMS 19050 Type 1A / 1B Unscreened Mining Feeder & Auxiliary – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/scgms-19050-type-1a-1b-unscreened-mining-feeder-auxiliary-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on Charbonnages de France SCGMS 19050 / NF M 82-375 / IEC 60245. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Mining std. | SCGMS 19050 (Charbonnages de France / NF M82)
Key data | Rated voltage | 0.6/1 kV (1kV) (Umax = 1.2 kV AC / 1.5 kV DC)
Key data | Conductor | Class 5 TCu (flexible stranded tinned copper)
Key data | Insulation | Cross-linked EPR (+90 °C continuous · +250 °C SC)
Key data | Outer sheath | Heavy PCP (EM2) (tear-, oil- & flame-retardant)
Key data | Min. bend R | 6 × OD (fixed) (8 × OD mobile semi-trailing)
Electrical | Rated voltage (U₀/U) | 0.6/1 kV AC (Umax = 1.2 kV AC / 1.5 kV DC)
Electrical | Routine AC dielectric test voltage | 3.0 kV / 3.5 kV AC rms for 5 minutes
Electrical | Max. conductor DC resistance @ 20 °C | Per NF EN 60228 Class 5 tinned copper
Thermal | Operating temperature range | −25 °C to +90 °C max. conductor · +250 °C short-circuit (5 s)
Thermal | Thermal cycling & overload stability | Verified thermal ageing and short-circuit withstand per standard
Mechanical | Outer sheath tear & abrasion resistance | Heavy-duty Polychloroprene (EM2 / 5GM3 grade) with inner elastomeric
Mechanical | Minimum bending radius | 6 × OD (fixed) · 8 × OD (mobile handling)
Resistance | Flame & oil resistance | NF C 32-070 C2 & IEC 60332-1-2 flame retardant · IRM 902 mineral oil
Resistance | Environmental & chemical durability | Resistant to moisture, industrial fluids and service ageing
Standards | Governing French mining standards | Charbonnages de France SCGMS 19050, NF M 82-375 & IEC 60245-4
Standards | Factory QA & material compliance | EN 10204 3.1 routine test certificate · RoHS 2 & REACH compliant
Identification | Core identification | Type 1A: HD 308 S2 (+ Green/Yellow) · Type 1B: Black numbered + G/Y
Identification | Customs tariff (HS) | 8544.49

## Construction
SCGMS 19050 Type 1A / 1B Unscreened Mining Feeder & Auxiliary – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/scgms-19050-type-1a-1b-unscreened-mining-feeder-auxiliary-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on Charbonnages de France SCGMS 19050 / NF M 82-375 / IEC 60245. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible stranded tinned copper (Class 5) | NF EN 60228 Class 5 annealed tinned copper (1.5 to 150 mm²)
2 | Cross-linked Ethylene Propylene Rubber (EPR) | 90 °C high-grade thermoset EPR compound (colour-coded on Type 1A, numbered on Type 1B)
3 | Extruded elastomeric inner bedding sheath | Pressure-extruded halogen-free/elastomeric inner covering filling core interstices
4 | Heavy-duty Polychloroprene (PCP / Neoprene) outer | Cross-linked chloroprene elastomer (Black or Yellow, high tear and oil resistance)
| SCGMS 19050 Type 1A (3G, 4G, 5G · 1.5 to 150 mm²) | Unscreened flexible low-voltage power feeder for underground pumps, fans and auxiliary switchgear
| SCGMS 19050 Type 1B (7G to 19G · 1.5 & 2.5 mm²) | Unscreened flexible multicore control, interlocking and tele-monitoring mining cable

## Quality and supply
SCGMS 19050 Type 1A / 1B Unscreened Mining Feeder & Auxiliary – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/scgms-19050-type-1a-1b-unscreened-mining-feeder-auxiliary-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on Charbonnages de France SCGMS 19050 / NF M 82-375 / IEC 60245. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.0 kV AC 5-min dielectric withstand & Class 5 tinned-Cu resistance test — Zero breakdown; conductor resistance within NF EN 60228 limits | Every drum
Sample test | PCP outer sheath hot-oil immersion, tear resistance & NF C 32-070 C2 flame test — Meets Charbonnages de France underground mining mechanical and flame criteria | Periodic audit
Standard / approval | Charbonnages de France SCGMS 19050 Compliant
Standard / approval | NF M 82-375 & NF C 32-070 C2 Flame Retardant
Standard / approval | CE, RoHS 2 & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | Embossed/printed: TEBAOFLEX SCGMS 19050 TYPE 1A (or 1B) 0.6/1kV <size> CE YEAR
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP