## Request a quote
Request a quotation for SCGMS 19050 Type 2A / 3A / 2B / 3B
Share your operating voltage, core configuration, and trailing/handler conditions for SCGMS 19050 Type 2A / 3A / 2B / 3B.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/scgms-19050-type-2a-3a-2b-3b-screened-underground-mining-trailing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SCGMS 19050 Type 2A / 3A / 2B / 3B Screened Underground Mining – Dimensions & weights (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/scgms-19050-type-2a-3a-2b-3b-screened-underground-mining-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF M 82-375 / SCGMS 19050. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Phase size mm² | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| SCGMS 19050 Type 2A 3×25+3E+1×6P (1000 V) | 3×25 + 3E + 1×6P (1000 V Type 2A) | 25 | 35.8 | 1020 | 1920 | 215 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
| SCGMS 19050 Type 2A 3×35+3E+1×6P (1000 V) | 3×35 + 3E + 1×6P (1000 V Type 2A) | 35 | 39.2 | 1350 | 2380 | 235 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
| SCGMS 19050 Type 2B 3×50+3E+1×10P (1000 V) | 3×50 + 3E + 1×10P (1000 V Type 2B) | 50 | 44.5 | 1860 | 3120 | 267 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
| SCGMS 19050 Type 2B 3×70+3E+1×10P (1000 V) | 3×70 + 3E + 1×10P (1000 V Type 2B) | 70 | 49.5 | 2540 | 4010 | 297 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
| SCGMS 19050 Type 2B 3×95+3E+1×10P (1000 V) | 3×95 + 3E + 1×10P (1000 V Type 2B) | 95 | 54.8 | 3420 | 5120 | 329 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
| SCGMS 19050 Type 3A 3×25+3E+1×10P (5.5 kV) | 3×25 + 3E + 1×10P (3.2/5.5 kV Type 3A) | 25 | 42.5 | 1090 | 2540 | 255 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
| SCGMS 19050 Type 3A 3×35+3E+1×10P (5.5 kV) | 3×35 + 3E + 1×10P (3.2/5.5 kV Type 3A) | 35 | 45.8 | 1410 | 3020 | 275 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
| SCGMS 19050 Type 3B 3×50+3E+1×10P (5.5 kV) | 3×50 + 3E + 1×10P (3.2/5.5 kV Type 3B) | 50 | 50.5 | 1910 | 3810 | 303 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
| SCGMS 19050 Type 3B 3×70+3E+1×10P (5.5 kV) | 3×70 + 3E + 1×10P (3.2/5.5 kV Type 3B) | 70 | 55.6 | 2610 | 4780 | 334 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
| SCGMS 19050 Type 3B 3×95+3E+1×10P (5.5 kV) | 3×95 + 3E + 1×10P (3.2/5.5 kV Type 3B) | 95 | 61 | 3510 | 5980 | 366 | Standard SCGMS 19050 Type 2A / 3A / 2B / 3B configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per NF M 82-375 / SCGMS 19050.

## Electrical & ampacity data
SCGMS 19050 Type 2A / 3A / 2B / 3B Screened Underground Mining – Electrical & ampacity data (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/scgms-19050-type-2a-3a-2b-3b-screened-underground-mining-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF M 82-375 / SCGMS 19050. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Current rating in air (A) | Current rating installed (A) | Mutual C pF/m ≈ | AC test V rms
3×25 + 3E + 1×6P (1000 V Type 2A) | 0.799 | 122 | 104 | 151 | 3500
3×35 + 3E + 1×6P (1000 V Type 2A) | 0.568 | 150 | 128 | 168 | 3500
3×50 + 3E + 1×10P (1000 V Type 2B) | 0.396 | 187 | 159 | 192 | 3500
3×70 + 3E + 1×10P (1000 V Type 2B) | 0.279 | 229 | 195 | 226 | 3500
3×95 + 3E + 1×10P (1000 V Type 2B) | 0.211 | 276 | 235 | 267 | 3500
3×25 + 3E + 1×10P (3.2/5.5 kV Type 3A) | 0.799 | 122 | 104 | 151 | 11000
3×35 + 3E + 1×10P (3.2/5.5 kV Type 3A) | 0.568 | 150 | 128 | 168 | 11000
3×50 + 3E + 1×10P (3.2/5.5 kV Type 3B) | 0.396 | 187 | 159 | 192 | 11000
3×70 + 3E + 1×10P (3.2/5.5 kV Type 3B) | 0.279 | 229 | 195 | 226 | 11000
3×95 + 3E + 1×10P (3.2/5.5 kV Type 3B) | 0.211 | 276 | 235 | 267 | 11000
Current ratings apply at +30 °C ambient in free air; apply standard derating factors for elevated ambient or drum layers.

## Technical data
SCGMS 19050 Type 2A / 3A / 2B / 3B Screened Underground Mining – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/scgms-19050-type-2a-3a-2b-3b-screened-underground-mining-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF M 82-375 / SCGMS 19050. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1000 V & 5500 V (0.6/1 kV (2A/2B) · 3.2/5.5 kV (3A/3B))
Key data | Standard | NF M 82-375 (Charbonnages de France SCGMS 19050)
Key data | Phase screen | Tinned Cu Braid (Individual phase earth/fault screen)
Key data | Insulation | +90 °C EPR (Cross-linked elastomer dielectric)
Key data | Outer sheath | Heavy PCP (Flame-retardant polychloroprene)
Key data | Min. bend radius | 6×D / 10×D (Fixed 6×D · trailing 10×D)
Electrical | Rated voltage U0/U | 0.6/1 kV (Type 2A/2B) · 3.2/5.5 kV (Type
Electrical | AC routine test voltage | 3.5 kV rms (Type 2A/2B) · 11 kV rms (Type
Electrical | Protective earth path | Combined conductance of the 3 tinned Cu
Electrical | Pilot core rating | 1 to 3 insulated/screened pilot cores for
Thermal | Max. conductor operating temp. | +90 °C continuous
Thermal | Max. short-circuit temperature | +250 °C (5 s)
Thermal | Ambient temperature range | -25 °C to +60 °C
Mechanical | Min. bending radius (fixed | 6 × D fixed · 10 × D trailing
Mechanical | Sheath reinforcement (Type 2B / 3B) | Embedded synthetic textile braid between
Mechanical | Max. tensile load on copper | 15–20 N/mm²
Resistance | Flame retardancy | NF C 32-070 C2 / IEC 60332-1-2 underground
Resistance | Oil & hydraulic fluid | NF EN 60811-404 resistant
Resistance | Impact & crush resistance | NF M 82-375 coal-face impact test
Standards | Primary specification | NF M 82-375 / Charbonnages de France SCGMS
Standards | Conductor standard | NF EN 60228 Class 5 tinned copper
Identification | Core coding | 3 screened phase cores + 1 to 3 pilot cores
Identification | Outer sheath colour | Yellow or Black with embossed NF M 82-375

## Construction
SCGMS 19050 Type 2A / 3A / 2B / 3B Screened Underground Mining – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/scgms-19050-type-2a-3a-2b-3b-screened-underground-mining-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF M 82-375 / SCGMS 19050. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Phase & pilot conductors | Finely stranded tinned annealed copper, Class 5 per NF EN 60228 | NF EN 60228 Class 5
2 | Central elastomeric cradle | Profiled rubber centre cradle positioning phase and pilot cores | NF M 82-375
3 | Stress-control layers (Type 3A/3B) | Inner and outer semi-conductive elastomeric layers on 3.2/5.5 kV cores | NF M 82-375
4 | EPR core insulation | Cross-linked ethylene propylene elastomer rated +90 °C (1000 V or 5500 V wall) | NF M 82-375
5 | Individual phase earth screens | Tinned copper wire/textile composite braid over each phase core forming the PE path | NF M 82-375 / SCGMS 19050
6 | Reinforced polychloroprene sheath | Extra-heavy flame-retardant, oil- and tear-resistant polychloroprene (with textile braid | NF M 82-375
| Type 2A & Type 2B (0.6/1 kV - 1000 V) | 1000 V phase-screened trailing cable (Type 2A standard; Type 2B reinforced anti-tear sheath).
| Type 3A & Type 3B (3.2/5.5 kV - 5500 V) | 5500 V MV phase-screened trailing cable (Type 3A standard; Type 3B reinforced anti-tear sheath).

## Quality and supply
SCGMS 19050 Type 2A / 3A / 2B / 3B Screened Underground Mining – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/scgms-19050-type-2a-3a-2b-3b-screened-underground-mining-trailing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on NF M 82-375 / SCGMS 19050. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage withstand test — 3.5 kV (Type 2A/2B) or 11 kV (Type 3A/3B) rms / 5 min | 100 % of drums
Routine test | Phase screen conductance check — NF M 82-375 protective earth screen resistance | 100 % of drums
Sample test | Coal-face impact & crush test — NF M 82-375 dynamic drop-weight impact test | Per production batch
Type test | Flame & oil resistance — NF C 32-070 C2 / IEC 60332-1-2 | Type approval
Standard / approval | NF M 82-375
Standard / approval | SCGMS 19050
Standard / approval | EN 10204 3.1
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX NF M 82-375 SCGMS 19050 TYPE
Supply | Delivery form: Fumigated export wooden drums
Supply | Standard drum lengths: 300 m · 500 m · 1000 m (or custom cut
Supply | MOQ: 100 m (stock sizes) · 300 m (custom build)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP