## Request a quote
Request a quotation for SCP / SYP
Application engineer · marine switchboard & JIS C 3410 wires
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/jis-shipboard-equipment-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SCP / SYP JIS Shipboard Equipment Wire – Dimensions & weights (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/jis-shipboard-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on JIS C 3410 (250 V Marine Switchboard Wire). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² / AWG | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| SCP 250V 1×0.75 | 1×0.75 | 18 | 2.9 | 3.2 | 7 | 17 | 13 | SCP 250 V EP-Rubber Switchboard Wires (+85/+90 °C, JIS C 3410)
| SCP 250V 1×1.25 | 1×1.25 | 16 | 3.3 | 3.6 | 12 | 23 | 14 | SCP 250 V EP-Rubber Switchboard Wires (+85/+90 °C, JIS C 3410)
| SCP 250V 1×1.5 | 1×1.5 | 16 | 3.5 | 3.8 | 14 | 27 | 15 | SCP 250 V EP-Rubber Switchboard Wires (+85/+90 °C, JIS C 3410)
| SCP 250V 1×2.0 | 1×2.0 | 14 | 3.8 | 4.1 | 19 | 33 | 16 | SCP 250 V EP-Rubber Switchboard Wires (+85/+90 °C, JIS C 3410)
| SCP 250V 1×2.5 | 1×2.5 | 14 | 4 | 4.4 | 24 | 39 | 18 | SCP 250 V EP-Rubber Switchboard Wires (+85/+90 °C, JIS C 3410)
| SCP 250V 1×3.5 | 1×3.5 | 12 | 4.5 | 4.9 | 33 | 52 | 20 | SCP 250 V EP-Rubber Switchboard Wires (+85/+90 °C, JIS C 3410)
| SCP 250V 1×5.5 | 1×5.5 | 10 | 5.2 | 5.7 | 52 | 76 | 23 | SCP 250 V EP-Rubber Switchboard Wires (+85/+90 °C, JIS C 3410)
| SYP 250V 1×0.75 | 1×0.75 | 18 | 2.5 | 2.7 | 7 | 13 | 11 | SYP 250 V Flame-Retardant Vinyl Switchboard Wires (JIS C 3410)
| SYP 250V 1×1.25 | 1×1.25 | 16 | 2.9 | 3.1 | 12 | 19 | 12 | SYP 250 V Flame-Retardant Vinyl Switchboard Wires (JIS C 3410)
| SYP 250V 1×1.5 | 1×1.5 | 16 | 3 | 3.3 | 14 | 22 | 13 | SYP 250 V Flame-Retardant Vinyl Switchboard Wires (JIS C 3410)
| SYP 250V 1×2.0 | 1×2.0 | 14 | 3.3 | 3.6 | 19 | 28 | 14 | SYP 250 V Flame-Retardant Vinyl Switchboard Wires (JIS C 3410)
| SYP 250V 1×2.5 | 1×2.5 | 14 | 3.6 | 3.9 | 24 | 34 | 16 | SYP 250 V Flame-Retardant Vinyl Switchboard Wires (JIS C 3410)
| SYP 250V 1×3.5 | 1×3.5 | 12 | 4 | 4.4 | 33 | 46 | 18 | SYP 250 V Flame-Retardant Vinyl Switchboard Wires (JIS C 3410)
| SYP 250V 1×5.5 | 1×5.5 | 10 | 4.8 | 5.2 | 52 | 69 | 21 | SYP 250 V Flame-Retardant Vinyl Switchboard Wires (JIS C 3410)
Dimensions and weights are typical values per JIS C 3410 (250 V Marine Switchboard Wire). Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
SCP / SYP JIS Shipboard Equipment Wire – Electrical & current ratings (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/jis-shipboard-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on JIS C 3410 (250 V Marine Switchboard Wire). Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single wire in air 30 °C, A | Multi-core bundle 30 °C, A
0.75 | 18 | 26.7 | 13 | 10
1.25 | 16 | 16 | 19 | 14
1.5 | 16 | 13.7 | 21 | 16
2 | 14 | 10.2 | 26 | 20
2.5 | 14 | 8.21 | 30 | 22
3.5 | 12 | 5.3 | 32 | 25
5.26 | 10 | 3.88 | 50 | 36
Current ratings at 30 °C ambient in free air. Apply temperature and bundle grouping factors per applicable equipment standard.

## Technical data
SCP / SYP JIS Shipboard Equipment Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/jis-shipboard-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on JIS C 3410 (250 V Marine Switchboard Wire). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 250 V (150/250 V AC · JIS C 3410 panel wire)
Key data | Test voltage | 1500 V AC (50/60 Hz 1–5 min dielectric test)
Key data | Thermal rating | +85/+90 & +75 °C (SCP: +85/+90 °C EPR · SYP: +75 °C PVC)
Key data | Flame test | IEC 60332-1-2 (Flame-retardant marine switchboard wire)
Key data | Bending radius | 4 × OD (4 × overall diameter fixed panel routing)
Key data | Size range | 0.75–5.5 mm² (7-wire or flexible stranded annealed Cu)
Electrical | Rated voltage | 250 V AC (150/250 V)
Electrical | AC test voltage (50/60 Hz) | 1500 V AC for 1–5 minutes
Electrical | Max. DC conductor resistance (20 °C) | 0.75 mm²: ≤ 25.3 Ω/km · 1.25 mm²: ≤ 15.0 Ω/km · 2.0 mm²: ≤ 9.42 Ω/km · 3.5 mm²: ≤ 5.30 Ω/km · 5.5 mm²: ≤ 3.40 Ω/km
Electrical | Insulation resistance (20 °C) | ≥ 1000 MΩ·km (SCP) · ≥ 50 MΩ·km (SYP)
Thermal | Max. conductor temperature | +85 °C / +90 °C continuous (SCP EP-rubber) · +60 °C / +75 °C continuous (SYP vinyl)
Thermal | Short-circuit temperature | +250 °C (SCP thermoset EPR) · +150 °C (SYP thermoplastic PVC)
Thermal | Ambient temperature range | −25 °C to +80 °C (SCP) · −15 °C to +60 °C (SYP)
Mechanical | Min. bending radius, fixed | 4 × overall diameter
Mechanical | Standard JIS cross-sections | 0.75, 1.25, 2.0, 3.5 and 5.5 mm² (plus IEC 1.5, 2.5 and 4.0 mm² equivalents)
Resistance | Flame retardance | JIS C 3005 / IEC 60332-1-2 self-extinguishing vertical flame test
Resistance | Oil & humidity resistance | Resistant to marine engine-room oil mist, condensation and salt-laden air
Standards | Primary standard | JIS C 3410 (Japanese Industrial Standard for Shipboard Cables)
Standards | IEC alignment | IEC 60092-350 & IEC 60092-353
Standards | Marine society scope | Accepted by NK, ABS, DNV, LR, BV and CCS for internal switchboard wiring
Standards | RoHS & SOLAS | RoHS 2 & SOLAS asbestos-free compliant
Identification | Insulation colours | White, Black, Red, Blue, Yellow, Green, Brown or Grey
Identification | Surface marking | TEBAOFLEX JIS C 3410 SCP / SYP 250V [Size]
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
SCP / SYP JIS Shipboard Equipment Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/jis-shipboard-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on JIS C 3410 (250 V Marine Switchboard Wire). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded annealed copper conductor | 7-wire circular stranded or flexible stranded annealed copper (tinned on SCP, bare/tinned on SYP) per JIS C 3102 / 3103 | JIS C 3410 / JIS C 3102
2 | Primary EPR (SCP) or Vinyl (SYP) layer | Cross-linked ethylene-propylene rubber (+85/+90 °C on SCP) or heat/flame-resistant PVC (+60/+75 °C on SYP) | JIS C 3410
3 | Protective flame-retardant outer skin | Oil- and flame-retardant polychloroprene / synthetic rubber skin (SCP) or colour-coded vinyl surface (SYP) | JIS C 3410 · IEC 60332-1-2
| SCP (250 V EP-Rubber Switchboard Wire, +85/+90 °C) | Thermoset EP-rubber insulated marine switchboard wire resistant to soldering heat and high ambient cubicles
| SYP (250 V Vinyl Switchboard Wire, +60/+75 °C) | Compact flame-retardant PVC insulated panel hook-up wire for relay racks and bridge indicator wiring

## Quality and supply
SCP / SYP JIS Shipboard Equipment Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/jis-shipboard-equipment-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on JIS C 3410 (250 V Marine Switchboard Wire). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage test — 1.5 kV AC (50/60 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / ASTM (tinned copper) | Every manufactured length
Sample test | Flame propagation test — IEC 60332-1-2 / UL VW-1 / ISO 6722-1 | Per production batch
Type test | Insulation & sheath material physical properties — JIS C 3410 (250 V Marine Switchboard Wire) | Type approval
Standard / approval | JIS C 3410 (250 V Marine Switchboard Wire)
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX JIS C 3410 SCP / SYP 250V [Size]
Supply | Delivery form: Export wooden drums, reels or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums or spools with sealed ends
Supply | Conductor / colour options: Custom core counts, stripe combinations or cut harnesses on request