## Request a quote
Request a quotation for SEOOW
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/seoow-tpe-portable-cord/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SEOOW TPE Portable Cord – Dimensions & masses (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/seoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | AWG × Conductors | Stranding / NEC Amps | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| SEOOW 18/3 | 18 AWG × 3C | 16/30 · 10 A | 9.27 | 26.2 | 98 | 55.6 | SEOOW size schedule
| SEOOW 18/4 | 18 AWG × 4C | 16/30 · 7 A | 10.03 | 35 | 118 | 60.2 | SEOOW size schedule
| SEOOW 16/3 | 16 AWG × 3C | 26/30 · 13 A | 9.91 | 41.7 | 118 | 59.5 | SEOOW size schedule
| SEOOW 16/4 | 16 AWG × 4C | 26/30 · 10 A | 10.67 | 55.6 | 145 | 64 | SEOOW size schedule
| SEOOW 14/3 | 14 AWG × 3C | 41/30 · 18 A | 13.34 | 66.3 | 205 | 80 | SEOOW size schedule
| SEOOW 14/4 | 14 AWG × 4C | 41/30 · 15 A | 14.48 | 88.4 | 250 | 86.9 | SEOOW size schedule
| SEOOW 12/3 | 12 AWG × 3C | 65/30 · 25 A | 15.11 | 105 | 275 | 90.7 | SEOOW size schedule
| SEOOW 12/4 | 12 AWG × 4C | 65/30 · 20 A | 16.51 | 140 | 345 | 99.1 | SEOOW size schedule
| SEOOW 10/3 | 10 AWG × 3C | 104/30 · 30 A | 16.76 | 168 | 380 | 100.6 | SEOOW size schedule
| SEOOW 10/4 | 10 AWG × 4C | 104/30 · 25 A | 18.16 | 224 | 475 | 109 | SEOOW size schedule
| SEOOW 8/3 | 8 AWG × 3C | 133/29 · 40 A | 21.08 | 267 | 610 | 126.5 | SEOOW size schedule
| SEOOW 8/4 | 8 AWG × 4C | 133/29 · 35 A | 23.11 | 356 | 765 | 138.7 | SEOOW size schedule
| SEOOW 6/3 | 6 AWG × 3C | 133/27 · 55 A | 23.88 | 425 | 860 | 143.3 | SEOOW size schedule
| SEOOW 6/4 | 6 AWG × 4C | 133/27 · 45 A | 26.16 | 566 | 1090 | 157 | SEOOW size schedule
| SEOOW 4/4 | 4 AWG × 4C | 133/25 · 60 A | 30.23 | 900 | 1620 | 181.4 | SEOOW size schedule
| SEOOW 2/4 | 2 AWG × 4C | 133/23 · 80 A | 34.8 | 1430 | 2380 | 208.8 | SEOOW size schedule
Dimensions and tolerances conform to UL 62 / CSA C22.2 No. 49 / NEC Art. 400.

## Electrical data
SEOOW TPE Portable Cord – Electrical data (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/seoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
AWG × Conductors | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
18 AWG × 3C | 21.4 | 10 | 8
18 AWG × 4C | 21.4 | 7 | 6
16 AWG × 3C | 13.5 | 13 | 10
16 AWG × 4C | 13.5 | 10 | 8
14 AWG × 3C | 8.45 | 18 | 14
14 AWG × 4C | 8.45 | 15 | 12
12 AWG × 3C | 5.31 | 25 | 20
12 AWG × 4C | 5.31 | 20 | 16
10 AWG × 3C | 3.34 | 30 | 24
10 AWG × 4C | 3.34 | 25 | 20
8 AWG × 3C | 2.1 | 40 | 32
8 AWG × 4C | 2.1 | 35 | 28
6 AWG × 3C | 1.32 | 55 | 44
6 AWG × 4C | 1.32 | 45 | 36
4 AWG × 4C | 0.83 | 60 | 48
2 AWG × 4C | 0.52 | 80 | 64
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
SEOOW TPE Portable Cord – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/seoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 600 V AC (UL 62 Extra-Hard Usage ('S'))
Key data | Elastomer ('E') | Heavy-wall TPE (Thermoplastic Elastomer core & sheath)
Key data | Temp window | -50 to +105 °C (Arctic sub-zero to +105 °C heat)
Key data | Oil & weather | OO + W rated (Double oil, UV & wet location)
Key data | Gauge range | 18 AWG to 2 AWG (10 A to 95 A portable feeders)
Key data | Min. bend radius | 6 × cord OD (Industrial reels, cranes & drops)
Electrical | Rated voltage | 600 V AC rms
Electrical | Dielectric withstand test | 2.0 kV AC rms for 1 minute
Electrical | NEC ampacity (3 current-carrying cores) | 10–30 A (18–10 AWG) · 40 A (8 AWG) · 55 A (6 AWG) · 70 A (4 AWG) · 95 A (2 AWG)
Thermal | Continuous operating temperature | -50 °C to +105 °C (UL 62 / CSA C22.2 No. 49)
Thermal | Arctic cold bend test | -50 °C for 4 hours without cracking
Mechanical | Insulation / jacket wall (16–10 AWG) | 0.76–1.14 mm (30–45 mil) insulation · 1.52–2.41 mm (60–95 mil) jacket
Mechanical | Insulation / jacket wall (8–2 AWG) | 1.14–1.52 mm (45–60 mil) insulation · 2.41–3.05 mm (95–120 mil) jacket
Resistance | Double oil & chemical resistance ('OO') | Both TPE core insulation and TPE jacket pass UL 62 oil immersion (+60/+100 °C)
Resistance | Weather, water & flame ('W') | UL 62 outdoor sunlight & wet location rated · UL VW-1 / CSA FT1/FT2 / MSHA flame
Standards | Reference standards | UL 62, CSA C22.2 No. 49 & NEC Article 400
Standards | Approvals | UL Listed Type SEOOW, CSA Certified, MSHA Approved, OSHA Acceptable
Identification | Code breakdown | S = Extra-Hard Service (600 V) · E = TPE Elastomer · OO = Double Oil · W = Weather/Outdoor
Identification | Core colour code | Black, White, Green, Red (+ Orange/Blue on 5C)

## Construction
SEOOW TPE Portable Cord – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/seoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible bunch / rope-stranded copper | Annealed bare copper (30 AWG wires in 18–10 AWG; rope-lay in 8–2 AWG) per UL 62 | ASTM B174
2 | 600 V oil-resistant TPE insulation (E + O) | Heavy-wall (0.76 to 1.52 mm) 105 °C / -50 °C thermoplastic elastomer core insulation | UL 62
3 | Non-wicking fibrillated fillers & binder | Absorbs tensile and torsional stresses while maintaining roundness for cord grips | UL 62
4 | Extra-hard-usage TPE jacket (O + W) | Heavy-wall (1.52 to 3.05 mm) oil-, UV-, chemical- and abrasion-resistant TPE outer sheath | UL 62
| SEOOW Control & Branch Power (18 AWG to 10 AWG — 2C to 5C) | 600 V Extra-Hard-Usage TPE cord for 480/600 V machine drops, pendants, festoons and cord reels.
| SEOOW Heavy Feeder (8 AWG, 6 AWG, 4 AWG & 2 AWG — 3C to 5C) | High-ampacity (40 A to 95 A) 600 V portable feeder cable for generator spider boxes, welders and mobile substations.

## Quality and supply
SEOOW TPE Portable Cord – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/seoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 2.0 kV AC dielectric test, spark test & DC resistance — Zero breakdown; resistance per UL 62 | 100 % of reels
Sample test | -50 °C cold bend & double oil immersion ('OO') — No cracking at -50 °C; core & jacket pass oil immersion | Every lot
Type test | 720-hour UV weathering, wet dielectric & VW-1/FT1/MSHA flame — UL Listed & CSA Certified to UL 62 / C22.2 No. 49 | Type qualification
Standard / approval | UL Listed Type SEOOW (600 V)
Standard / approval | CSA Certified C22.2 No. 49 (FT1 / FT2)
Standard / approval | MSHA Flame Approved
Standard / approval | NEC Article 400 Extra-Hard Usage
Standard / approval | RoHS 3 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) SEOOW [N/AWG] 600V 105C -50C TPE WATER RESISTANT CSA FT1 FT2 P-MSHA [lot/ft]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP