## Request a quote
Request a quotation for SJEOOW
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/sjeoow-tpe-portable-cord/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SJEOOW TPE Portable Cord – Dimensions & masses (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjeoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | AWG × Conductors | Stranding / NEC Amps | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| SJEOOW 18/2 | 18 AWG × 2C | 16/30 · 10 A | 7.24 | 17.5 | 58 | 36.2 | SJEOOW size schedule
| SJEOOW 18/3 | 18 AWG × 3C | 16/30 · 10 A | 7.75 | 26.2 | 72 | 38.8 | SJEOOW size schedule
| SJEOOW 18/4 | 18 AWG × 4C | 16/30 · 7 A | 8.51 | 35 | 90 | 42.5 | SJEOOW size schedule
| SJEOOW 16/2 | 16 AWG × 2C | 26/30 · 13 A | 7.87 | 27.8 | 73 | 39.4 | SJEOOW size schedule
| SJEOOW 16/3 | 16 AWG × 3C | 26/30 · 13 A | 8.38 | 41.7 | 92 | 41.9 | SJEOOW size schedule
| SJEOOW 16/4 | 16 AWG × 4C | 26/30 · 10 A | 9.27 | 55.6 | 118 | 46.3 | SJEOOW size schedule
| SJEOOW 14/2 | 14 AWG × 2C | 41/30 · 18 A | 9.02 | 44.2 | 102 | 45.1 | SJEOOW size schedule
| SJEOOW 14/3 | 14 AWG × 3C | 41/30 · 18 A | 9.53 | 66.3 | 132 | 47.6 | SJEOOW size schedule
| SJEOOW 14/4 | 14 AWG × 4C | 41/30 · 15 A | 10.54 | 88.4 | 168 | 52.7 | SJEOOW size schedule
| SJEOOW 12/3 | 12 AWG × 3C | 65/30 · 25 A | 11.05 | 105 | 188 | 55.2 | SJEOOW size schedule
| SJEOOW 12/4 | 12 AWG × 4C | 65/30 · 20 A | 12.07 | 140 | 240 | 60.4 | SJEOOW size schedule
| SJEOOW 10/3 | 10 AWG × 3C | 104/30 · 30 A | 14.35 | 168 | 312 | 71.8 | SJEOOW size schedule
| SJEOOW 10/4 | 10 AWG × 4C | 104/30 · 25 A | 15.75 | 224 | 398 | 78.8 | SJEOOW size schedule
Dimensions and tolerances conform to UL 62 / CSA C22.2 No. 49 / NEC Art. 400.

## Electrical data
SJEOOW TPE Portable Cord – Electrical data (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjeoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
AWG × Conductors | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
18 AWG × 2C | 21.4 | 10 | 8
18 AWG × 3C | 21.4 | 10 | 8
18 AWG × 4C | 21.4 | 7 | 6
16 AWG × 2C | 13.5 | 13 | 10
16 AWG × 3C | 13.5 | 13 | 10
16 AWG × 4C | 13.5 | 10 | 8
14 AWG × 2C | 8.45 | 18 | 14
14 AWG × 3C | 8.45 | 18 | 14
14 AWG × 4C | 8.45 | 15 | 12
12 AWG × 3C | 5.31 | 25 | 20
12 AWG × 4C | 5.31 | 20 | 16
10 AWG × 3C | 3.34 | 30 | 24
10 AWG × 4C | 3.34 | 25 | 20
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
SJEOOW TPE Portable Cord – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjeoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300 V AC (UL 62 Junior Hard Service (SJ))
Key data | Elastomer ('E') | TPE core & jacke (Thermoplastic Elastomer compound)
Key data | Temp window | -50 to +105 °C (10 °C colder flex than PVC SJTOOW)
Key data | Oil & weather | OO + W rated (Double oil, sunlight & water proof)
Key data | Gauge range | 18 to 10 AWG (2, 3, 4 & 5 conductors)
Key data | Min. bend radius | 5 × cord OD (Sub-zero reels & portable tools)
Electrical | Rated voltage | 300 V AC rms
Electrical | Dielectric withstand test | 1.5 kV AC rms for 1 minute
Electrical | NEC ampacity (3 current-carrying cores) | 10 A (18 AWG) · 13 A (16 AWG) · 18 A (14 AWG) · 25 A (12 AWG) · 30 A (10 AWG)
Thermal | Continuous operating temperature | -50 °C to +105 °C (UL 62 / CSA C22.2 No. 49)
Thermal | Arctic cold bend test | -50 °C for 4 hours on mandrel without cracking
Mechanical | Nom. insulation / jacket wall (16–12 AWG) | 0.76 mm (30 mil) TPE insulation · 1.52 mm (60 mil) TPE jacket
Mechanical | Specific gravity advantage | 12–18 % lighter than equivalent PVC SJTOOW or rubber SJOOW
Resistance | Double oil resistance ('OO') | Both TPE core insulation and TPE jacket pass UL 62 oil immersion
Resistance | Sunlight, water & flame ('W') | UL 62 outdoor wet location & UV rated · UL VW-1 / CSA FT2 flame
Standards | Reference standards | UL 62, CSA C22.2 No. 49 & NEC Article 400
Standards | Approvals | UL Listed, CSA Certified, MSHA Approved option, RoHS 3
Identification | Code breakdown | S = Service · J = Junior (300 V) · E = Thermoplastic Elastomer (TPE) · OO = Double Oil · W = Weather/Outdoor
Identification | Core colour code | Black, White, Green (+ Red, Orange)

## Construction
SJEOOW TPE Portable Cord – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjeoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible bunch-stranded copper (ASTM B174) | Fine-stranded annealed bare copper (30 AWG wires) per UL 62 | ASTM B174
2 | Oil-resistant TPE core insulation (E + O) | 105 °C / -50 °C thermoplastic elastomer insulation with colour coding and oil immunity | UL 62
3 | Non-wicking fibrillated fillers & separator | Keeps core lay concentric and strips cleanly without talcum powder residue | UL 62
4 | Oil & arctic-weather TPE jacket (O + W) | Low-density, non-marking thermoplastic elastomer outer sheath (-50 °C to +105 °C) | UL 62
| SJEOOW Black / Yellow / Blue Industrial Grade | 300 V TPE double oil-resistant cord in high-visibility safety colours or matte black stage finish.
| SJEOOW Shielded Option | Available with 85 % tinned copper braid or foil/braid shield for VFD/sensor portable drops.

## Quality and supply
SJEOOW TPE Portable Cord – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjeoow-tpe-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1.5 kV AC dielectric test, spark test & DC resistance — Zero breakdown; resistance per UL 62 | 100 % of reels
Sample test | -50 °C cold mandrel bend & double oil immersion ('OO') — Zero cracks at -50 °C; passes core & jacket oil test | Every lot
Type test | 720-hour UV weathering, water absorption & VW-1/FT2 flame — UL Listed & CSA Certified to UL 62 / C22.2 No. 49 | Type qualification
Standard / approval | UL Listed Type SJEOOW
Standard / approval | CSA Certified C22.2 No. 49 (FT2)
Standard / approval | NEC Article 400 Compliant
Standard / approval | OSHA & MSHA Acceptable
Standard / approval | RoHS 3 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) SJEOOW [N/AWG] 300V 105C -50C TPE WATER RESISTANT CSA FT2 [lot/ft]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP