## Request a quote
Request a quotation for SJTOW
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/sjtow-outdoor-portable-cord/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SJTOW Outdoor Portable Cord – Dimensions & masses (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjtow-outdoor-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | AWG × Conductors | Stranding / NEC Amps | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| SJTOW 18/2 | 18 AWG × 2C | 16/30 · 10 A | 7.37 | 17.5 | 66 | 44.2 | SJTOW size schedule
| SJTOW 18/3 | 18 AWG × 3C | 16/30 · 10 A | 7.87 | 26.2 | 81 | 47.2 | SJTOW size schedule
| SJTOW 18/4 | 18 AWG × 4C | 16/30 · 7 A | 8.64 | 35 | 100 | 51.8 | SJTOW size schedule
| SJTOW 16/2 | 16 AWG × 2C | 26/30 · 13 A | 8 | 27.8 | 81 | 48 | SJTOW size schedule
| SJTOW 16/3 | 16 AWG × 3C | 26/30 · 13 A | 8.51 | 41.7 | 103 | 51.1 | SJTOW size schedule
| SJTOW 16/4 | 16 AWG × 4C | 26/30 · 10 A | 9.4 | 55.6 | 130 | 56.4 | SJTOW size schedule
| SJTOW 14/2 | 14 AWG × 2C | 41/30 · 18 A | 9.14 | 44.2 | 114 | 54.8 | SJTOW size schedule
| SJTOW 14/3 | 14 AWG × 3C | 41/30 · 18 A | 9.65 | 66.3 | 145 | 57.9 | SJTOW size schedule
| SJTOW 14/4 | 14 AWG × 4C | 41/30 · 15 A | 10.67 | 88.4 | 184 | 64 | SJTOW size schedule
| SJTOW 12/3 | 12 AWG × 3C | 65/30 · 25 A | 11.18 | 105 | 206 | 67.1 | SJTOW size schedule
| SJTOW 12/4 | 12 AWG × 4C | 65/30 · 20 A | 12.19 | 140 | 262 | 73.1 | SJTOW size schedule
| SJTOW 10/3 | 10 AWG × 3C | 104/30 · 30 A | 14.48 | 168 | 342 | 86.9 | SJTOW size schedule
Dimensions and tolerances conform to UL 62 / CSA C22.2 No. 49 / NEC Art. 400.

## Electrical data
SJTOW Outdoor Portable Cord – Electrical data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjtow-outdoor-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
AWG × Conductors | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
18 AWG × 2C | 21.4 | 10 | 8
18 AWG × 3C | 21.4 | 10 | 8
18 AWG × 4C | 21.4 | 7 | 6
16 AWG × 2C | 13.5 | 13 | 10
16 AWG × 3C | 13.5 | 13 | 10
16 AWG × 4C | 13.5 | 10 | 8
14 AWG × 2C | 8.45 | 18 | 14
14 AWG × 3C | 8.45 | 18 | 14
14 AWG × 4C | 8.45 | 15 | 12
12 AWG × 3C | 5.31 | 25 | 20
12 AWG × 4C | 5.31 | 20 | 16
10 AWG × 3C | 3.34 | 30 | 24
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
SJTOW Outdoor Portable Cord – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjtow-outdoor-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300 V AC (UL 62 Junior Hard Service (SJ))
Key data | Polymer type | Thermoplastic PV (-40 °C to +105 °C (or +60/+90 °C))
Key data | Oil rating | Single 'O' (Jack (Oil-resistant outer PVC sheath)
Key data | Weather rating | 'W' Outdoor / We (UV sunlight & water resistant)
Key data | Gauge range | 18 to 10 AWG (2, 3 & 4 conductors)
Key data | Min. bend radius | 6 × cord OD (Extension cords & power tools)
Electrical | Rated voltage | 300 V AC rms
Electrical | Dielectric withstand test | 1.5 kV AC rms for 1 minute
Electrical | NEC ampacity (3 current-carrying cores) | 10 A (18 AWG) · 13 A (16 AWG) · 18 A (14 AWG) · 25 A (12 AWG) · 30 A (10 AWG)
Thermal | Continuous temperature range | -40 °C to +105 °C (UL / CSA)
Thermal | Cold bend test | -40 °C without jacket cracking
Mechanical | Insulation / jacket wall (18–12 AWG) | 0.76 mm (30 mil) insulation · 1.52 mm (60 mil) jacket
Mechanical | Minimum bending radius | 6 × overall cord diameter
Resistance | Outer jacket oil resistance ('O') | Outer PVC sheath passes UL 62 oil immersion without swelling or cracking
Resistance | Outdoor & flame rating ('W') | 720 h Xenon-arc UV & wet location rated · UL VW-1 / CSA FT2 flame
Standards | Reference standards | UL 62, CSA C22.2 No. 49 & NEC Article 400
Standards | Safety compliance | UL Listed, CSA Certified, OSHA Acceptable, RoHS 3
Identification | Code breakdown | S = Service · J = Junior (300 V) · T = Thermoplastic PVC · O = Oil-resistant jacket · W = Weather/Outdoor
Identification | Core colour code | Black, White, Green (+ Red on 4C)

## Construction
SJTOW Outdoor Portable Cord – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjtow-outdoor-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible bunch-stranded copper (ASTM B174) | Fine-stranded annealed bare copper (30 AWG individual strands) per UL 62 | ASTM B174
2 | Thermoplastic PVC core insulation (T) | Moisture- and heat-resistant colour-coded PVC dielectric (0.76–1.14 mm wall) | UL 62
3 | Polypropylene fillers & separator wrap | Provides a smooth round profile for watertight cord grips | UL 62
4 | Oil & outdoor PVC outer jacket (O + W) | Oil-resistant, UV-stabilised and water-resistant PVC outer sheath | UL 62
| SJTOW Outdoor Contractor Grade (Yellow / Orange / Blue) | High-visibility 300 V outdoor extension and power tool cord in 16/3, 14/3, 12/3 and 10/3 AWG.
| SJTOW OEM Appliance Grade (Black / Grey) | Black or grey 300 V cord for pressure washers, compressors, fans and commercial appliances.

## Quality and supply
SJTOW Outdoor Portable Cord – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/sjtow-outdoor-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1.5 kV AC dielectric test, spark test & DC resistance — Zero breakdown; resistance per UL 62 | 100 % of reels
Sample test | Outer jacket oil immersion & -40 °C cold bend test — Jacket passes UL 62 oil & low-temperature bend | Every batch
Type test | 720-hour UV weathering, wet dielectric & VW-1/FT2 flame — UL Listed & CSA Certified to UL 62 / C22.2 No. 49 | Type qualification
Standard / approval | UL Listed Type SJTOW
Standard / approval | CSA Certified C22.2 No. 49 (FT2)
Standard / approval | NEC Article 400 Compliant
Standard / approval | OSHA Acceptable
Standard / approval | RoHS 3 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) SJTOW [N/AWG] 300V 105C -40C OUTDOOR WATER RESISTANT CSA FT2 [lot/ft]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP