## Request a quote
Request a quotation for SS-LDN
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nylon-jacketed-linear-heat-detection-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SS-LDN Nylon-Jacketed Linear Heat Detection Cable – Dimensions & masses (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nylon-jacketed-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Alarm Temp & Amb. | Core Ø mm | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| SS-LDN-68 (68 °C Nylon LHD) | 68 °C PA12 (Amb ≤45 °C) | 2×0.85 mm | 4.2 | 12 | 27 | 63 | SS-LDN standard series
| SS-LDN-78 (78 °C Nylon LHD) | 78 °C PA12 (Amb ≤55 °C) | 2×0.85 mm | 4.2 | 12 | 27 | 63 | SS-LDN standard series
| SS-LDN-85 (85 °C Nylon LHD) | 85 °C PA12 (Amb ≤65 °C) | 2×0.85 mm | 4.2 | 12 | 27 | 63 | SS-LDN standard series
| SS-LDN-95 (95 °C Nylon LHD) | 95 °C PA12 (Amb ≤70 °C) | 2×0.85 mm | 4.2 | 12 | 27 | 63 | SS-LDN standard series
| SS-LDN-105 (105 °C Nylon LHD) | 105 °C PA12 (Amb ≤85 °C) | 2×0.85 mm | 4.3 | 12 | 28 | 64 | SS-LDN standard series
| SS-LDN-138 (138 °C Nylon LHD) | 138 °C PA12 (Amb ≤105 °C) | 2×0.85 mm | 4.4 | 12 | 30 | 66 | SS-LDN standard series
| SS-LDN-68-MSG (68 °C + Messenger) | 68 °C PA12 + SS Messenger | 2×0.85 mm | 6.8 | 12 | 48 | 102 | SS-LDN standard series
| SS-LDN-85-MSG (85 °C + Messenger) | 85 °C PA12 + SS Messenger | 2×0.85 mm | 6.8 | 12 | 48 | 102 | SS-LDN standard series
| SS-LDN-105-MSG (105 °C + Messenger) | 105 °C PA12 + SS Messenger | 2×0.85 mm | 6.9 | 12 | 49 | 104 | SS-LDN standard series
| SS-LDN-138-MSG (138 °C + Messenger) | 138 °C PA12 + SS Messenger | 2×0.85 mm | 7 | 12 | 51 | 105 | SS-LDN standard series
| SS-LDN-85-4C (85 °C 4-Core PA12) | 85 °C 4C Redundant PA12 | 4×0.85 mm | 5.8 | 24 | 49 | 87 | SS-LDN standard series
| SS-LDN-105-4C (105 °C 4-Core PA12) | 105 °C 4C Redundant PA12 | 4×0.85 mm | 5.9 | 24 | 51 | 88 | SS-LDN standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per EN 54-28 / UL 521.

## Electrical data
SS-LDN Nylon-Jacketed Linear Heat Detection Cable – Electrical data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nylon-jacketed-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Alarm Temp & Amb. | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
68 °C PA12 (Amb ≤45 °C) | 98 | 1 | 1
78 °C PA12 (Amb ≤55 °C) | 98 | 1 | 1
85 °C PA12 (Amb ≤65 °C) | 98 | 1 | 1
95 °C PA12 (Amb ≤70 °C) | 98 | 1 | 1
105 °C PA12 (Amb ≤85 °C) | 98 | 1 | 1
138 °C PA12 (Amb ≤105 °C) | 98 | 1 | 1
68 °C PA12 + SS Messenger | 98 | 1 | 1
85 °C PA12 + SS Messenger | 98 | 1 | 1
105 °C PA12 + SS Messenger | 98 | 1 | 1
138 °C PA12 + SS Messenger | 98 | 1 | 1
85 °C 4C Redundant PA12 | 98 | 1 | 1
105 °C 4C Redundant PA12 | 98 | 1 | 1
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
SS-LDN Nylon-Jacketed Linear Heat Detection Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nylon-jacketed-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Alarm ratings | 68 / 85 / 105 / (Fixed digital switching temps)
Key data | Outer jacket | PA12 Nylon (UV-stabilised black polyamide 12)
Key data | Sensing cores | 2 × spring steel (Tinned copper-clad spring steel)
Key data | Loop resistance | ≈100 Ω/km (Per core (distance location ready))
Key data | Ambient range | -40 to +105 °C (Outdoor UV & chemical resistant)
Key data | Min. bend radius | 65 mm (≈15×OD) (Fixed clip & rim mounting)
Electrical | Max. operating voltage | 42 VDC / 30 VAC
Electrical | Conductor DC resistance | ≈100 Ω/km per conductor (200 Ω/km loop)
Electrical | Dielectric test voltage | 500 VAC rms for 1 minute
Thermal | Alarm temperature ratings | 68 °C · 78 °C · 85 °C · 105 °C · 138 °C
Thermal | Max. continuous ambient temp. | 45 °C (68 °C) · 65 °C (85 °C) · 85 °C (105 °C) · 105 °C (138 °C)
Thermal | Operating temperature floor | -40 °C
Mechanical | Nominal outer diameter | 4.2 mm ± 0.2 mm
Mechanical | Min. installation bend radius | 65 mm (≈15 × cable OD)
Mechanical | Abrasion & cut-through | High-hardness Shore D 72 PA12 nylon outer skin
Resistance | Hydrocarbon & solvent resistance | Resists crude oil, diesel, jet fuel, benzene, dilute acids & alkalis
Resistance | UV weather resistance | Carbon-black stabilised PA12 per UL 1581 / ISO 4892 UV exposure
Resistance | Flame retardancy | IEC 60332-1-2 / UL 1581 VW-1
Standards | Product standard | EN 54-28 & UL 521
Standards | Hazardous area suitability | Simple apparatus per IEC 60079-11 when connected via Zener/galvanic IS barrier
Identification | Outer jacket colour | Jet Black (UV-stabilised PA12) with colour-coded print legend
Identification | Core colours | Red & White insulated sensing cores

## Construction
SS-LDN Nylon-Jacketed Linear Heat Detection Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nylon-jacketed-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Spring-steel sensing conductors | Two twisted high-tensile tinned copper-clad spring-steel wires under constant radial contact pressure | EN 54-28
2 | Calibrated thermo-reactive polymer | Temperature-calibrated thermoplastic polymer melting at 68, 85, 105 or 138 °C | EN 54-28
3 | Flame-retardant inner sheath | Primary moisture-blocking flame-retardant polymer inner jacket | EN 54-28
4 | PA12 nylon protective jacket | Extruded UV-stabilised carbon-black Polyamide 12 (PA12) chemical- and oil-resistant outer jacket | EN 54-28
| SS-LDN-68 (68 °C / 155 °F) | Max ambient +45 °C — outdoor covered conveyors, chemical warehouses and tank farms in temperate climates.
| SS-LDN-85 (85 °C / 185 °F) | Max ambient +65 °C — direct-sunlight floating-roof tank rim seals, outdoor pipe racks and solar arrays.
| SS-LDN-105 (105 °C / 221 °F) | Max ambient +85 °C — refinery process units, hot oil lines, desert tank rims and chemical reactors.
| SS-LDN-138 (138 °C / 280 °F) | Max ambient +105 °C — high-temperature steam tracing manifolds and petrochemical reformer zones.

## Quality and supply
SS-LDN Nylon-Jacketed Linear Heat Detection Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nylon-jacketed-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 500 VAC dielectric & loop DC resistance test — Zero fault prior to activation; 100 Ω/km ±3 % per core | 100 % of reels
Sample test | Fluid immersion & thermal response test — No jacket cracking after hydrocarbon immersion; exact trip temperature per EN 54-28 | Batch sample
Type test | UV xenon-arc weathering & EN 54-28 response — Retains tensile strength and thermal trip accuracy after accelerated UV exposure | Type qualification
Standard / approval | EN 54-28 Compliant
Standard / approval | UL 521 Design
Standard / approval | IEC 60079-11 Simple Apparatus (with IS barrier)
Standard / approval | ISO 4892 UV Stabilised
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX SS-LDN-85 NYLON JACKETED LINEAR HEAT DETECTION CABLE 85C PA12 UV/OIL RES EN 54-28 [meter mark]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP