## Request a quote
Request a quotation for SS-LDS
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/stainless-steel-protected-linear-heat-detection-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SS-LDS Stainless-Steel-Protected Linear Heat Detection Cable – Dimensions & masses (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/stainless-steel-protected-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Alarm Temp & Armour | Core Ø mm | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| SS-LDS-68 (68 °C + SS304 Braid) | 68 °C SS304 (Amb ≤45 °C) | 2×0.85 mm | 4.5 | 12 | 38 | 72 | SS-LDS standard series
| SS-LDS-78 (78 °C + SS304 Braid) | 78 °C SS304 (Amb ≤55 °C) | 2×0.85 mm | 4.5 | 12 | 38 | 72 | SS-LDS standard series
| SS-LDS-85 (85 °C + SS304 Braid) | 85 °C SS304 (Amb ≤65 °C) | 2×0.85 mm | 4.5 | 12 | 38 | 72 | SS-LDS standard series
| SS-LDS-95 (95 °C + SS304 Braid) | 95 °C SS304 (Amb ≤70 °C) | 2×0.85 mm | 4.5 | 12 | 38 | 72 | SS-LDS standard series
| SS-LDS-105 (105 °C + SS304 Braid) | 105 °C SS304 (Amb ≤85 °C) | 2×0.85 mm | 4.6 | 12 | 39 | 74 | SS-LDS standard series
| SS-LDS-138 (138 °C + SS304 Braid) | 138 °C SS304 (Amb ≤105 °C) | 2×0.85 mm | 4.7 | 12 | 41 | 75 | SS-LDS standard series
| SS-LDNS-68 (68 °C PA12 + SS316) | 68 °C PA12+SS316 | 2×0.85 mm | 4.9 | 12 | 44 | 78 | SS-LDS standard series
| SS-LDNS-85 (85 °C PA12 + SS316) | 85 °C PA12+SS316 | 2×0.85 mm | 4.9 | 12 | 44 | 78 | SS-LDS standard series
| SS-LDNS-105 (105 °C PA12 + SS316) | 105 °C PA12+SS316 | 2×0.85 mm | 5 | 12 | 45 | 80 | SS-LDS standard series
| SS-LDNS-138 (138 °C PA12 + SS316) | 138 °C PA12+SS316 | 2×0.85 mm | 5.1 | 12 | 47 | 82 | SS-LDS standard series
| SS-LDS-85-LSZH (85 °C LSZH + SS304) | 85 °C LSZH+SS304 | 2×0.85 mm | 4.6 | 12 | 40 | 74 | SS-LDS standard series
| SS-LDS-105-LSZH (105 °C LSZH + SS304) | 105 °C LSZH+SS304 | 2×0.85 mm | 4.7 | 12 | 41 | 75 | SS-LDS standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per EN 54-28 / UL 521.

## Electrical data
SS-LDS Stainless-Steel-Protected Linear Heat Detection Cable – Electrical data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/stainless-steel-protected-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Alarm Temp & Armour | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
68 °C SS304 (Amb ≤45 °C) | 98 | 1 | 1
78 °C SS304 (Amb ≤55 °C) | 98 | 1 | 1
85 °C SS304 (Amb ≤65 °C) | 98 | 1 | 1
95 °C SS304 (Amb ≤70 °C) | 98 | 1 | 1
105 °C SS304 (Amb ≤85 °C) | 98 | 1 | 1
138 °C SS304 (Amb ≤105 °C) | 98 | 1 | 1
68 °C PA12+SS316 | 98 | 1 | 1
85 °C PA12+SS316 | 98 | 1 | 1
105 °C PA12+SS316 | 98 | 1 | 1
138 °C PA12+SS316 | 98 | 1 | 1
85 °C LSZH+SS304 | 98 | 1 | 1
105 °C LSZH+SS304 | 98 | 1 | 1
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
SS-LDS Stainless-Steel-Protected Linear Heat Detection Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/stainless-steel-protected-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Alarm ratings | 68 / 85 / 105 / (Fixed digital switching temps)
Key data | Armour braid | AISI 304 / 316 S (≥85 % stainless-steel wire braid)
Key data | Sensing cores | 2 × spring steel (Tinned copper-clad spring steel)
Key data | Loop resistance | ≈100 Ω/km (Per conductor (distance locating))
Key data | Ambient range | -40 to +105 °C (Heavy mechanical & rodent protection)
Key data | Min. bend radius | 75 mm (≈16×OD) (Armoured clip & bracket routing)
Electrical | Max. operating voltage | 42 VDC / 30 VAC
Electrical | Nominal DC resistance | ≈100 Ω/km per conductor (200 Ω/km loop)
Electrical | Braid earthing | Stainless-steel outer braid must be earthed at one end to drain induced EMI
Thermal | Alarm temperature classes | 68 °C · 78 °C · 85 °C · 105 °C · 138 °C
Thermal | Max. continuous ambient temp. | 45 °C (68 °C) · 65 °C (85 °C) · 85 °C (105 °C) · 105 °C (138 °C)
Thermal | Min. operating temp. | -40 °C
Mechanical | Nominal outer diameter | 4.6 mm ± 0.2 mm (4.9 mm on PA12+SS)
Mechanical | Min. installation bend radius | 75 mm
Mechanical | Crush & cut-through resistance | >1500 N radial crush resistance without false trip
Resistance | Rodent & abrasion resistance | Woven AISI 304/316 stainless-steel wire armour
Resistance | Corrosion resistance | Salt-mist, acid-mine water & industrial washdown resistant
Resistance | Flame retardancy | IEC 60332-1-2
Standards | Detection standard | EN 54-28 & UL 521
Standards | Intrinsic safety compatibility | Simple apparatus per IEC 60079-11 with Ex ia barrier
Identification | Outer appearance | Bright woven stainless-steel braid over colour-coded inner sheath
Identification | Tagging | Stamped stainless-steel or colour-coded marker sleeves at 5 m intervals

## Construction
SS-LDS Stainless-Steel-Protected Linear Heat Detection Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/stainless-steel-protected-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Spring-steel sensing conductors | Two twisted high-tensile tinned copper-clad spring-steel wires held under radial spring force | EN 54-28
2 | Calibrated thermo-reactive polymer | Temperature-sensitive polymer compound calibrated to yield at 68, 85, 105 or 138 °C | EN 54-28
3 | Flame-retardant inner jacket | Extruded PVC, LSZH or PA12 nylon environmental barrier sheath | EN 54-28
4 | Stainless-steel wire braid armour | Close-woven AISI 304 (or marine AISI 316) stainless-steel wire braid providing crush, impact, rodent and EMC protection | EN 54-28
| SS-LDS (PVC/LSZH + AISI 304 Braid) | Standard stainless-steel braided LHD cable for conveyors, tunnels, car parks and industrial cable trays.
| SS-LDNS (PA12 Nylon + AISI 316 Braid) | Combines a chemical/UV-resistant PA12 nylon jacket with marine-grade AISI 316 stainless-steel braid for offshore and petrochemical zones.

## Quality and supply
SS-LDS Stainless-Steel-Protected Linear Heat Detection Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/stainless-steel-protected-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 500 VAC core-to-core & core-to-braid dielectric test — Zero fault between sensing cores and stainless braid | 100 % of reels
Sample test | Radial crush & thermal activation bath test — No false trip under mechanical load; trips accurately at rated °C | Every batch
Type test | EN 54-28 thermal response & salt-spray corrosion test — Braid and inner sheath pass ISO 9227 neutral salt spray | Type qualification
Standard / approval | EN 54-28 Compliant
Standard / approval | UL 521 Design
Standard / approval | IEC 60079-11 Simple Apparatus
Standard / approval | ISO 9227 Salt-Spray Tested
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX SS-LDS-85 STAINLESS STEEL BRAIDED LHD CABLE 85C AISI 304 EN 54-28
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP