## Request a quote
Request a quotation for SS-LD
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/digital-linear-heat-detection-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SS-LD Digital Linear Heat Detection Cable – Dimensions & masses (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/digital-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Alarm Temp & Amb. | Core Ø mm | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| SS-LD-68-PVC (68 °C Digital LHD) | 68 °C (Amb ≤45 °C) | 2×0.85 mm | 3.6 | 12 | 22 | 54 | SS-LD standard series
| SS-LD-68-LSZH (68 °C LSZH LHD) | 68 °C LSZH (Amb ≤45 °C) | 2×0.85 mm | 3.7 | 12 | 24 | 56 | SS-LD standard series
| SS-LD-78-PVC (78 °C Digital LHD) | 78 °C (Amb ≤55 °C) | 2×0.85 mm | 3.6 | 12 | 22 | 54 | SS-LD standard series
| SS-LD-78-LSZH (78 °C LSZH LHD) | 78 °C LSZH (Amb ≤55 °C) | 2×0.85 mm | 3.7 | 12 | 24 | 56 | SS-LD standard series
| SS-LD-85-PVC (85 °C Digital LHD) | 85 °C (Amb ≤65 °C) | 2×0.85 mm | 3.6 | 12 | 22 | 54 | SS-LD standard series
| SS-LD-85-LSZH (85 °C LSZH LHD) | 85 °C LSZH (Amb ≤65 °C) | 2×0.85 mm | 3.7 | 12 | 24 | 56 | SS-LD standard series
| SS-LD-95-PVC (95 °C Digital LHD) | 95 °C (Amb ≤70 °C) | 2×0.85 mm | 3.6 | 12 | 22 | 54 | SS-LD standard series
| SS-LD-105-PVC (105 °C Digital LHD) | 105 °C (Amb ≤85 °C) | 2×0.85 mm | 3.7 | 12 | 23 | 56 | SS-LD standard series
| SS-LD-105-LSZH (105 °C LSZH LHD) | 105 °C LSZH (Amb ≤85 °C) | 2×0.85 mm | 3.8 | 12 | 25 | 57 | SS-LD standard series
| SS-LD-138-HT (138 °C Digital LHD) | 138 °C (Amb ≤105 °C) | 2×0.85 mm | 3.8 | 12 | 26 | 57 | SS-LD standard series
| SS-LD-180-HT (180 °C Fluoropolymer) | 180 °C (Amb ≤150 °C) | 2×0.85 mm | 3.9 | 12 | 29 | 58 | SS-LD standard series
| SS-LD-68-4C (Dual-Circuit 68 °C) | 68 °C 4-Core Redundant | 4×0.85 mm | 5.2 | 24 | 42 | 78 | SS-LD standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per EN 54-28 / UL 521.

## Electrical data
SS-LD Digital Linear Heat Detection Cable – Electrical data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/digital-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Alarm Temp & Amb. | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
68 °C (Amb ≤45 °C) | 98 | 1 | 1
68 °C LSZH (Amb ≤45 °C) | 98 | 1 | 1
78 °C (Amb ≤55 °C) | 98 | 1 | 1
78 °C LSZH (Amb ≤55 °C) | 98 | 1 | 1
85 °C (Amb ≤65 °C) | 98 | 1 | 1
85 °C LSZH (Amb ≤65 °C) | 98 | 1 | 1
95 °C (Amb ≤70 °C) | 98 | 1 | 1
105 °C (Amb ≤85 °C) | 98 | 1 | 1
105 °C LSZH (Amb ≤85 °C) | 98 | 1 | 1
138 °C (Amb ≤105 °C) | 98 | 1 | 1
180 °C (Amb ≤150 °C) | 98 | 1 | 1
68 °C 4-Core Redundant | 98 | 1 | 1
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
SS-LD Digital Linear Heat Detection Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/digital-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Alarm ratings | 68 / 85 / 105 / (Fixed activation temperatures)
Key data | Max. loop voltage | 42 VDC / 30 VAC (Low-voltage fire alarm monitor loop)
Key data | Sensing cores | 2 × spring steel (Copper-clad / tinned spring steel)
Key data | Loop resistance | ≈100 Ω/km (Per conductor (distance location))
Key data | Ambient range | -40 to +105 °C (Grade dependent (45 °C to 105 °C max))
Key data | Min. bend radius | 50 mm (≈15×OD) (Clip & tray installation)
Electrical | Max. operating voltage | 42 VDC / 30 VAC
Electrical | Nominal conductor DC resistance | ≈100 Ω/km per core (200 Ω/km loop for distance location)
Electrical | Dielectric withstand (untriggered) | 500 VAC rms for 1 minute
Electrical | Max. zone length | Up to 2000–3000 m per distance-locating controller zone
Thermal | Alarm temperature classes | 68 °C · 78 °C · 85 °C · 105 °C · 138 °C · 180 °C
Thermal | Max. continuous ambient temp. | 45 °C (68 °C grade) · 65 °C (85 °C grade) · 85 °C (105 °C grade) · 105 °C (138 °C grade)
Thermal | Min. operating temperature | -40 °C (-60 °C cold-store grade)
Mechanical | Nominal outer diameter | 3.6 mm ± 0.2 mm
Mechanical | Min. installation bend radius | 50 mm (≈15 × cable OD)
Mechanical | Recommended support clip spacing | 0.8 m to 1.2 m using insulated J-clips or Z-brackets
Resistance | Flame retardancy | IEC 60332-1-2 / UL 1581 VW-1
Resistance | Humidity & dust immunity | IP67 sealed extruded sheath unaffected by dust or condensation
Standards | European product standard | EN 54-28 (Non-resettable line-type heat detectors)
Standards | North American standard | UL 521 / FM 3210
Identification | Sheath colour coding | Red (68/85 °C), White, Orange (105 °C) or Blue (138 °C)
Identification | Core polarity | Red & White/Black insulated spring-steel cores

## Construction
SS-LD Digital Linear Heat Detection Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/digital-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Spring-steel sensing conductors | Two twisted high-tensile tinned copper-clad spring-steel wires (0.8–0.9 mm Ø) held under radial contact tension | EN 54-28
2 | Calibrated thermo-reactive polymer | Precision-extruded temperature-sensitive polymer dielectric that yields sharply at its rated alarm temperature | EN 54-28
3 | Protective separation tape | Thin polyester protective binder tape over twisted sensing pair | EN 54-28
4 | Flame-retardant outer jacket | Moisture- and flame-retardant PVC or LSZH outer sheath (colour-coded by alarm temperature: Red, White, Orange, Blue) | EN 54-28
| SS-LD-68 (68 °C / 155 °F) | Max ambient +45 °C — general cable trays, offices, warehouses, escalators and cold-store ceilings (Red sheath).
| SS-LD-85 (85 °C / 185 °F) | Max ambient +65 °C — warm plant rooms, solar roof voids, car parks and enclosed conveyors (White/Red sheath).
| SS-LD-105 (105 °C / 221 °F) | Max ambient +85 °C — boiler houses, turbine hoods, transformer rooms and high-temp cable tunnels (Orange sheath).
| SS-LD-138 (138 °C / 280 °F) | Max ambient +105 °C — industrial drying ovens, steam pipe proximity and steelworks galleries (Blue/Black sheath).

## Quality and supply
SS-LD Digital Linear Heat Detection Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/digital-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-28 / UL 521. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 500 VAC dielectric withstand & loop resistance calibration — No premature contact; calibrated Ω/km resistance within ±3 % | 100 % of reels
Sample test | Oven bath activation temperature accuracy test — Triggers strictly within rated temperature window per EN 54-28 | Every production batch
Type test | EN 54-28 / UL 521 environmental & response-time qualification — Verified thermal response time across wind speeds and orientations | Type approval
Standard / approval | EN 54-28 Compliant
Standard / approval | UL 521 / FM 3210 Design
Standard / approval | IEC 60332-1-2 Flame Retardant
Standard / approval | RoHS 3 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX SS-LD-85 DIGITAL LINEAR HEAT DETECTION CABLE 85C (185F) MAX AMB 65C EN 54-28 [meter mark]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP