## Request a quote
Request a quotation for STOOW
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/stoow-thermoplastic-portable-cord/#template-selection
An application engineer replies within 2 business hours.

## Sizes
STOOW Thermoplastic Portable Cord – Dimensions & masses (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/stoow-thermoplastic-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | AWG × Conductors | Stranding / NEC Amps | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| STOOW 18/3 | 18 AWG × 3C | 16/30 · 10 A | 9.4 | 26.2 | 112 | 56.4 | STOOW size schedule
| STOOW 18/4 | 18 AWG × 4C | 16/30 · 7 A | 10.16 | 35 | 135 | 61 | STOOW size schedule
| STOOW 16/3 | 16 AWG × 3C | 26/30 · 13 A | 10.03 | 41.7 | 134 | 60.2 | STOOW size schedule
| STOOW 16/4 | 16 AWG × 4C | 26/30 · 10 A | 10.8 | 55.6 | 165 | 64.8 | STOOW size schedule
| STOOW 14/3 | 14 AWG × 3C | 41/30 · 18 A | 13.46 | 66.3 | 232 | 80.8 | STOOW size schedule
| STOOW 14/4 | 14 AWG × 4C | 41/30 · 15 A | 14.61 | 88.4 | 282 | 87.7 | STOOW size schedule
| STOOW 12/3 | 12 AWG × 3C | 65/30 · 25 A | 15.24 | 105 | 310 | 91.4 | STOOW size schedule
| STOOW 12/4 | 12 AWG × 4C | 65/30 · 20 A | 16.64 | 140 | 388 | 99.8 | STOOW size schedule
| STOOW 10/3 | 10 AWG × 3C | 104/30 · 30 A | 16.89 | 168 | 425 | 101.3 | STOOW size schedule
| STOOW 10/4 | 10 AWG × 4C | 104/30 · 25 A | 18.29 | 224 | 530 | 109.7 | STOOW size schedule
| STOOW 8/4 | 8 AWG × 4C | 133/29 · 35 A | 23.37 | 356 | 855 | 140.2 | STOOW size schedule
| STOOW 6/4 | 6 AWG × 4C | 133/27 · 45 A | 26.42 | 566 | 1210 | 158.5 | STOOW size schedule
Dimensions and tolerances conform to UL 62 / CSA C22.2 No. 49 / NEC Art. 400.

## Electrical data
STOOW Thermoplastic Portable Cord – Electrical data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/stoow-thermoplastic-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
AWG × Conductors | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
18 AWG × 3C | 21.4 | 10 | 8
18 AWG × 4C | 21.4 | 7 | 6
16 AWG × 3C | 13.5 | 13 | 10
16 AWG × 4C | 13.5 | 10 | 8
14 AWG × 3C | 8.45 | 18 | 14
14 AWG × 4C | 8.45 | 15 | 12
12 AWG × 3C | 5.31 | 25 | 20
12 AWG × 4C | 5.31 | 20 | 16
10 AWG × 3C | 3.34 | 30 | 24
10 AWG × 4C | 3.34 | 25 | 20
8 AWG × 4C | 2.1 | 35 | 28
6 AWG × 4C | 1.32 | 45 | 36
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
STOOW Thermoplastic Portable Cord – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/stoow-thermoplastic-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 600 V AC (UL 62 Extra-Hard Usage ('S'))
Key data | Polymer type | Thermoplastic PV (105 °C oil- & heat-stabilised)
Key data | Oil & weather | OO + W rated (Core + jacket oil & outdoor wet)
Key data | Gauge range | 18 AWG to 2 AWG (2, 3, 4 & 5 conductors)
Key data | Operating temp | -40 to +105 °C (Indoor plant & outdoor jobsites)
Key data | Min. bend radius | 6 × cord OD (Machine drops & pendant controls)
Electrical | Rated voltage | 600 V AC rms
Electrical | Dielectric withstand test | 2.0 kV AC rms for 1 minute
Electrical | NEC ampacity (3 current-carrying cores) | 10–30 A (18–10 AWG) · 40 A (8 AWG) · 55 A (6 AWG) · 70 A (4 AWG) · 95 A (2 AWG)
Thermal | Continuous operating temperature | -40 °C to +105 °C (UL 62 / CSA C22.2 No. 49)
Thermal | Cold bend test | -40 °C for 4 hours without cracking
Mechanical | Insulation / jacket wall (16–10 AWG) | 0.76–1.14 mm (30–45 mil) insulation · 1.52–2.41 mm (60–95 mil) jacket
Mechanical | Insulation / jacket wall (8–2 AWG) | 1.14–1.52 mm (45–60 mil) insulation · 2.41–3.05 mm (95–120 mil) jacket
Resistance | Double oil resistance ('OO') | Both PVC core insulation and PVC outer jacket pass UL 62 oil immersion
Resistance | Weather & flame rating ('W') | UL 62 outdoor sunlight & wet location rated · UL VW-1 / CSA FT1 / FT2 flame
Standards | Reference standards | UL 62, CSA C22.2 No. 49 & NEC Article 400
Standards | Approvals | UL Listed Type STOOW, CSA Certified, OSHA Acceptable, RoHS 3
Identification | Code breakdown | S = Extra-Hard Service (600 V) · T = Thermoplastic PVC · OO = Double Oil · W = Weather/Outdoor
Identification | Core colour code | Black, White, Green, Red (+ Orange/Blue)

## Construction
STOOW Thermoplastic Portable Cord – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/stoow-thermoplastic-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible bunch / rope-stranded copper | Annealed bare copper (30 AWG wires in 18–10 AWG; rope-stranded in 8–2 AWG) per UL 62 | ASTM B174
2 | 600 V oil-resistant PVC insulation (T + O) | Heavy-wall (0.76 to 1.52 mm) 105 °C oil- and moisture-resistant PVC core insulation | UL 62
3 | Polypropylene fillers & separator wrap | Maintains circular cross-section for liquid-tight cord grips | UL 62
4 | Extra-hard-usage PVC jacket (O + W) | Heavy-wall (1.52 to 3.05 mm) oil-, UV-, acid/alkali- and water-resistant PVC outer sheath | UL 62
| STOOW Yellow Safety Jacket (18 AWG to 2 AWG) | High-visibility safety yellow 600 V double oil-resistant PVC portable cord.
| STOOW Black / Grey Industrial Jacket | Black or machine-tool grey 600 V double oil-resistant PVC cord for factory equipment drops.

## Quality and supply
STOOW Thermoplastic Portable Cord – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/stoow-thermoplastic-portable-cord/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Art. 400. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 2.0 kV AC dielectric test, spark test & DC resistance — Zero breakdown; resistance per UL 62 | 100 % of reels
Sample test | Double oil immersion ('OO') & -40 °C cold bend — Core & jacket pass UL 62 oil and low-temp wind | Every batch
Type test | 720-hour UV weathering, wet dielectric & VW-1/FT1 flame — UL Listed & CSA Certified to UL 62 / C22.2 No. 49 | Type qualification
Standard / approval | UL Listed Type STOOW (600 V)
Standard / approval | CSA Certified C22.2 No. 49 (FT1 / FT2)
Standard / approval | NEC Article 400 Extra-Hard Usage
Standard / approval | OSHA Acceptable
Standard / approval | RoHS 3 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (UL) STOOW [N/AWG] 600V 105C -40C WATER RESISTANT CSA FT1 FT2 [lot/ft]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP