## Request a quote
Request a quotation for SUBCAB Power and Monitoring
Application engineer · submersible & pump cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/submersible-pump-power-and-monitoring-hybrid-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SUBCAB Power and Monitoring – Dimensions & weights (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/submersible-pump-power-and-monitoring-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / DIN VDE 0250. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| SUBCAB 3G1.5+2×1.5 | 3G1.5+2×1.5 | 16 | 12 | 13 | 72 | 225 | 52 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G1.5+2×1.5 | 4G1.5+2×1.5 | 16 | 13.1 | 14.2 | 86 | 265 | 57 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G2.5+2×1.5 | 4G2.5+2×1.5 | 14 | 14.7 | 16 | 125 | 345 | 64 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G4+2×1.5 | 4G4+2×1.5 | 12 | 16.4 | 17.8 | 182 | 455 | 71 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G6+2×1.5 | 4G6+2×1.5 | 10 | 18.2 | 19.8 | 259 | 595 | 79 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G10+2×1.5 | 4G10+2×1.5 | 8 | 21.7 | 23.6 | 413 | 910 | 94 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G16+2×1.5 | 4G16+2×1.5 | 6 | 24.8 | 27 | 643 | 1265 | 108 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G25+2×1.5 | 4G25+2×1.5 | 4 | 29.6 | 32.2 | 989 | 1850 | 129 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G35+2×1.5 | 4G35+2×1.5 | 2 | 32.9 | 35.8 | 1373 | 2410 | 143 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G50+2×1.5 | 4G50+2×1.5 | 1 | 37.9 | 41.2 | 1949 | 3290 | 165 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 4G70+2×1.5 | 4G70+2×1.5 | 2/0 | 42.8 | 46.5 | 2717 | 4380 | 186 | 4G Power + 2×1.5 mm² Monitoring Hybrid Configurations (1.5–70 mm²)
| SUBCAB 3×95+3G16+2×1.5 | 3×95+3G16+2×1.5 | 3/0 | 45.8 | 49.8 | 3226 | 5120 | 199 | 3×Phase + 3G Split Earth + 2×1.5 mm² High-Power Pump Configurations (95–120 mm²)
| SUBCAB 3×120+3G16+2×1.5 | 3×120+3G16+2×1.5 | 4/0 | 49.7 | 54 | 3946 | 6150 | 216 | 3×Phase + 3G Split Earth + 2×1.5 mm² High-Power Pump Configurations (95–120 mm²)
Dimensions and weights are typical values per EN 50525-2-21 AD8 / DIN VDE 0250. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
SUBCAB Power and Monitoring – Electrical & current ratings (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/submersible-pump-power-and-monitoring-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / DIN VDE 0250. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
1.5 | 16 | 13.3 | 23 | 18
2.5 | 14 | 7.98 | 30 | 25
4 | 12 | 4.95 | 41 | 34
6 | 10 | 3.3 | 53 | 44
10 | 8 | 1.91 | 74 | 61
16 | 6 | 1.21 | 99 | 82
25 | 4 | 0.78 | 131 | 108
35 | 2 | 0.554 | 162 | 135
50 | 1 | 0.386 | 202 | 168
70 | 2/0 | 0.272 | 250 | 207
95 | 3/0 | 0.206 | 301 | 250
120 | 4/0 | 0.161 | 352 | 292
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
SUBCAB Power and Monitoring – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/submersible-pump-power-and-monitoring-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / DIN VDE 0250. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (0.6/1 kV power · 3.0 kV AC test)
Key data | Water depth | Up to 500 m (AD8 permanent submersion (50 bar))
Key data | Water temp. | +70 °C max. (+90 °C max. conductor temp.)
Key data | Ambient temp. | −25…+80 °C (Flexing (−40…+80 °C fixed))
Key data | Bending radius | 4–6 × OD (4 × OD fixed · 6 × OD flexing)
Key data | Hybrid layout | 3–4P + 2×1.5 (Power 1.5–120 mm² + sensor cores)
Electrical | Rated voltage (power cores) | 450/750 V / 0.6/1 kV U0/U (max. 1200 V AC)
Electrical | Rated voltage (control cores) | 300/500 V U0/U (thermal & seal sensor circuits)
Electrical | AC test voltage | 3000 V AC on power cores · 2000 V AC on control cores
Electrical | Conductor stranding | IEC 60228 Class 5 fine-stranded copper
Electrical | Current rating basis | DIN VDE 0298-4 (+90 °C EPR conductor rating)
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Max. water temperature | +70 °C continuous submersion
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Ambient temperature range | −25 °C to +80 °C flexing · −40 °C to +80 °C fixed
Mechanical | Min. bending radius, fixed | 4 × overall diameter
Mechanical | Min. bending radius, moving | 6 × overall diameter
Mechanical | Max. tensile load | 15 N/mm² of total copper cross-section
Mechanical | Max. submersion depth | 500 m water column (50 bar hydrostatic pressure, AD8)
Resistance | Water & sewage resistance | AD8 permanent immersion in wastewater, sludge & seawater (pH 3–10)
Resistance | Oil & grease resistance | EN 60811-404 mineral oil & effluent grease resistant
Resistance | Flame retardance | IEC 60332-1-2 self-extinguishing
Resistance | Ozone, UV & abrasion | EN 60811-403 ozone-resistant chlorinated elastomer jacket
Standards | Construction basis | EN 50525-2-21 (AD8) & DIN VDE 0250
Standards | Conductor standard | IEC 60228 / EN 60228 Class 5
Standards | Submersion classification | HD 384 / IEC 60364-5-51 Class AD8
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Black
Identification | Core identification | Power: HD 308 S2 (brown, black, grey + GN/YE) · Control: black numbered T1, T2
Identification | Sheath marking | TEBAOFLEX SUBCAB [Size] 450/750V-0.6/1kV AD8 SUBMERSIBLE PUMP CABLE CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
SUBCAB Power and Monitoring – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/submersible-pump-power-and-monitoring-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / DIN VDE 0250. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Power & monitoring conductors | Fine-stranded bare or tinned copper wire (IEC 60228 Class 5): 3–4 power cores + 2×1.5 mm² control cores | IEC 60228 Class 5
2 | Water-resistant EPR insulation | Cross-linked ethylene-propylene rubber compound Type 3GI3 / EI4 (+90 °C rated, low water absorption) | DIN VDE 0207-20 3GI3
3 | Inner elastomeric bedding | Extruded water-blocking elastomeric filler consolidating power and control cores into a tight circular profile
4 | Heavy-duty AD8 outer sheath | Cross-linked chlorinated elastomer / polychloroprene (CSM/PCP, Type 5GM5 / EM2), black
| SUBCAB 4G + 2×1.5 mm² | 3 phase cores + 1 green-yellow earth + 2 numbered 1.5 mm² pilot/monitoring cores (1.5 to 70 mm²)
| SUBCAB 3× + 3G/3 + 2×1.5 mm² | Symmetrical 3 phase cores + 3 split interstitial earth cores + 2×1.5 mm² control cores (95 to 120 mm²)
| SUBCAB Screened S3× + S(2×0.5) | EMC-screened VFD pump power construction with individually screened control pair for analog/bus sensors

## Quality and supply
SUBCAB Power and Monitoring – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/submersible-pump-power-and-monitoring-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 AD8 / DIN VDE 0250. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 3.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — EN 50525-2-21 AD8 / DIN VDE 0250 | Type approval
Standard / approval | EN 50525-2-21 AD8 / DIN VDE 0250
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX SUBCAB [Size] 450/750V-0.6/1kV AD8 SUBMERSIBLE PUMP CABLE CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request