## Request a quote
Request a quotation for Securiton SEC 15 / SEC 20
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/sec-15-sec-20-copper-tube-sensing-element-linear-heat-detection-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Securiton SEC 15 / SEC 20 Copper-Tube Sensing Element Linear Heat – Dimensions & masses (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sec-15-sec-20-copper-tube-sensing-element-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-22 / VdS. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Type & Coil Length | OD / ID mm | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| SEC 15 Bare Cu Tube (50 m Coil) | SEC 15 Bare Cu · 50 m | 5.0 / 3.0 mm | 5 | 112 | 112 | 50 | Securiton SEC 15 / SEC 20 standard series
| SEC 15 Bare Cu Tube (100 m Coil) | SEC 15 Bare Cu · 100 m | 5.0 / 3.0 mm | 5 | 112 | 112 | 50 | Securiton SEC 15 / SEC 20 standard series
| SEC 20-RD Red Sheathed (50 m Coil) | SEC 20 Red PE/HF · 50 m | 6.2 / 3.0 mm | 6.2 | 112 | 128 | 62 | Securiton SEC 15 / SEC 20 standard series
| SEC 20-RD Red Sheathed (100 m Coil) | SEC 20 Red PE/HF · 100 m | 6.2 / 3.0 mm | 6.2 | 112 | 128 | 62 | Securiton SEC 15 / SEC 20 standard series
| SEC 20-BK Black UV Sheathed (50 m) | SEC 20 Black UV · 50 m | 6.2 / 3.0 mm | 6.2 | 112 | 128 | 62 | Securiton SEC 15 / SEC 20 standard series
| SEC 20-BK Black UV Sheathed (100 m) | SEC 20 Black UV · 100 m | 6.2 / 3.0 mm | 6.2 | 112 | 128 | 62 | Securiton SEC 15 / SEC 20 standard series
| SEC 20-GY Grey Sheathed (50 m Coil) | SEC 20 Grey HF · 50 m | 6.2 / 3.0 mm | 6.2 | 112 | 128 | 62 | Securiton SEC 15 / SEC 20 standard series
| SEC 20-GY Grey Sheathed (100 m Coil) | SEC 20 Grey HF · 100 m | 6.2 / 3.0 mm | 6.2 | 112 | 128 | 62 | Securiton SEC 15 / SEC 20 standard series
| SEC 15-SS Stainless Tube 5/3 (50 m) | AISI 316Ti Tube · 50 m | 5.0 / 3.0 mm | 5 | 0 | 100 | 50 | Securiton SEC 15 / SEC 20 standard series
| SEC 15-SS Stainless Tube 5/3 (100 m) | AISI 316Ti Tube · 100 m | 5.0 / 3.0 mm | 5 | 0 | 100 | 50 | Securiton SEC 15 / SEC 20 standard series
| SEC 20-SS Sheathed Stainless (50 m) | Sheathed AISI 316Ti · 50 m | 6.2 / 3.0 mm | 6.2 | 0 | 116 | 62 | Securiton SEC 15 / SEC 20 standard series
| SEC 20-SS Sheathed Stainless (100 m) | Sheathed AISI 316Ti · 100 m | 6.2 / 3.0 mm | 6.2 | 0 | 116 | 62 | Securiton SEC 15 / SEC 20 standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per EN 54-22 / VdS.

## Electrical data
Securiton SEC 15 / SEC 20 Copper-Tube Sensing Element Linear Heat – Electrical data (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sec-15-sec-20-copper-tube-sensing-element-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-22 / VdS. Values for your order are confirmed in the quotation.
Type & Coil Length | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
SEC 15 Bare Cu · 50 m | 1.45 | 0 | 0
SEC 15 Bare Cu · 100 m | 1.45 | 0 | 0
SEC 20 Red PE/HF · 50 m | 1.45 | 0 | 0
SEC 20 Red PE/HF · 100 m | 1.45 | 0 | 0
SEC 20 Black UV · 50 m | 1.45 | 0 | 0
SEC 20 Black UV · 100 m | 1.45 | 0 | 0
SEC 20 Grey HF · 50 m | 1.45 | 0 | 0
SEC 20 Grey HF · 100 m | 1.45 | 0 | 0
AISI 316Ti Tube · 50 m | 58 | 0 | 0
AISI 316Ti Tube · 100 m | 58 | 0 | 0
Sheathed AISI 316Ti · 50 m | 58 | 0 | 0
Sheathed AISI 316Ti · 100 m | 58 | 0 | 0
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
Securiton SEC 15 / SEC 20 Copper-Tube Sensing Element Linear Heat – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/sec-15-sec-20-copper-tube-sensing-element-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-22 / VdS. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | EN 54-22 (Resettable line-type heat detector)
Key data | Tube geometry | 5.0 / 3.0 mm (5 mm OD × 3 mm ID (1.0 mm Cu wall))
Key data | Sensing principle | Pneumatic Δp/Δt (Rate-of-rise & max temp diaphragm)
Key data | Tube variants | SEC 15 / SEC 20 (Bare Cu (SEC 15) · Sheathed (SEC 20))
Key data | Ambient range | -40 to +200 °C (Bare Cu +200 °C · Sheathed +80 °C)
Key data | Min. bend radius | 50 mm (Formed capillary tube bends)
Electrical | Electrical energy in sensing tube | 0 V / 0 mA (100 % passive pneumatic tube; intrinsically safe in ATEX Zones 0, 1, 2, 20, 21, 22)
Electrical | EMI & lightning immunity | 100 % immune to electromagnetic fields, HV catenary induction and radiation
Thermal | EN 54-22 response classes | Class A1I, A2I, BI, CI (programmable via evaluation unit)
Thermal | Operating temperature (SEC 15 bare Cu) | -40 °C to +200 °C continuous
Thermal | Operating temperature (SEC 20 sheathed) | -40 °C to +80 °C continuous
Mechanical | Copper tube dimensions | 5.0 mm OD × 3.0 mm ID × 1.0 mm wall (SEC 15) · 6.2 mm OD with sheath (SEC 20)
Mechanical | Minimum bending radius | 50 mm (hand-formed or bending-roller radius)
Mechanical | Max. sensing tube loop length | Up to 120–150 m per pneumatic evaluation chamber
Resistance | Corrosion & chemical resistance | SEC 20 halogen-free sheath resists tunnel exhaust condensates, road salt, acids and alkalis
Resistance | Resettable fire survival | Automatically resets after thermal transients below copper annealing/melting threshold
Standards | European product standard | EN 54-22 (Resettable line-type heat detectors) & VdS approval
Standards | Copper tube metallurgy | EN 12449 Cu-DHP (CW024A) seamless drawn tube
Identification | Tube finish & colours | SEC 15: Bright bare copper · SEC 20: Red (RAL 3000), Black (UV) or Grey
Identification | Coil marking | Stamped lot number, 5/3 mm tube dimensions and EN 54-22 system tag

## Construction
Securiton SEC 15 / SEC 20 Copper-Tube Sensing Element Linear Heat – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/sec-15-sec-20-copper-tube-sensing-element-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-22 / VdS. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Seamless copper capillary tube (SEC 15) | Precision-drawn annealed seamless phosphorus-deoxidized copper tube (Cu-DHP CW024A), 5.0 mm OD × 3.0 mm ID (1.0 mm wall) | EN 12449
2 | Enclosed pneumatic air column | Hermetically monitored dry air volume (3.0 mm bore) transmitting Gay-Lussac thermal pressure waves to the evaluation diaphragm | EN 54-22
3 | Halogen-free protective sheath (SEC 20) | Extruded 0.6 mm halogen-free polyethylene / polyamide corrosion-protection jacket (5.0 → 6.2 mm OD, Red, Black or Grey on SEC 20) | EN 54-22
| SEC 15 (Bare Copper Tube 5/3 mm) | Uninsulated 5.0 mm OD × 3.0 mm ID seamless copper sensing tube for fastest thermal response and ambients up to +200 °C.
| SEC 20 (Halogen-Free Sheathed Cu Tube 6.2/3 mm) | 5/3 mm seamless copper tube with a 0.6 mm halogen-free PE/LSZH outer sheath against road-tunnel de-icing salt, exhaust acids and ammonia.

## Quality and supply
Securiton SEC 15 / SEC 20 Copper-Tube Sensing Element Linear Heat – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/sec-15-sec-20-copper-tube-sensing-element-linear-heat-detection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 54-22 / VdS. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Pneumatic pressure decay & hermetical leak test — 100 % pressure-hold verification at 5 bar with zero micro-leaks | 100 % of coils
Routine test | Internal bore calibration & plugged-end check — Verified 3.0 mm ± 0.05 mm internal diameter and dry nitrogen purge | 100 % of coils
Type test | EN 54-22 Class A1I / A2I / BI / CI wind-tunnel response test — Certified rate-of-rise and maximum temperature alarm response | VdS / EN 54-22 qualification
Standard / approval | EN 54-22 Class A1I / A2I / BI / CI
Standard / approval | VdS System Compatibility
Standard / approval | EN 12449 Seamless Cu-DHP
Standard / approval | ATEX Passive Non-Electrical Sensor
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | SEC 20 5x1mm Cu-DHP + 0.6mm HF SHEATH EN 54-22 LINEAR HEAT SENSING TUBE [lot/coil]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP