## Request a quote
Request a quotation for Self-Regulating Heat Tracing Cable
Application engineer · industrial heat-tracing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/self-regulating-heat-tracing-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Self-Regulating Heat Tracing Cable – Power ratings, temperatures & dimensions (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/self-regulating-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Model designation | Rated Vac | Thermal series | Output @10°C W/m | Max maintain °C | Max exposure °C | T-class (IEC) | Bus wire mm² | Width × Thick. mm | Mass ≈ kg/km
| 10LSR2-CT · 230 V | 230 Vac | LSR (Low) | 10 | 65 | 85 | T6 | 1.25 | 10.5 × 5.2 | 115
| 15LSR2-CT · 230 V | 230 Vac | LSR (Low) | 15 | 65 | 85 | T6 | 1.25 | 10.5 × 5.2 | 118
| 20LSR2-CT · 230 V | 230 Vac | LSR (Low) | 20 | 65 | 85 | T6 | 1.25 | 11.2 × 5.4 | 124
| 25LSR2-CT · 230 V | 230 Vac | LSR (Low) | 25 | 65 | 85 | T6 | 1.25 | 11.2 × 5.4 | 126
| 30LSR2-CT · 230 V | 230 Vac | LSR (Low) | 30 | 65 | 85 | T6 | 1.25 | 11.6 × 5.5 | 132
| 15LSR1-CT · 120 V | 120 Vac | LSR (Low) | 15 | 65 | 85 | T6 | 1.25 | 10.5 × 5.2 | 118
| 25LSR1-CT · 120 V | 120 Vac | LSR (Low) | 25 | 65 | 85 | T6 | 1.25 | 11.2 × 5.4 | 126
| 15MSR2-CT · 230 V | 230 Vac | MSR (Medium) | 15 | 110 | 135 | T4 | 1.5 | 11.8 × 5.6 | 138
| 30MSR2-CT · 230 V | 230 Vac | MSR (Medium) | 30 | 110 | 135 | T4 | 1.5 | 11.8 × 5.6 | 142
| 45MSR2-CT · 230 V | 230 Vac | MSR (Medium) | 45 | 110 | 135 | T4 | 1.5 | 12.2 × 5.8 | 148
| 30MSR1-CT · 120 V | 120 Vac | MSR (Medium) | 30 | 110 | 135 | T4 | 1.5 | 11.8 × 5.6 | 142
| 15HSR2-CT · 230 V | 230 Vac | HSR (High) | 15 | 150 | 215 | T3 | 2 | 12.4 × 6.0 | 162
| 30HSR2-CT · 230 V | 230 Vac | HSR (High) | 30 | 150 | 215 | T3 | 2 | 12.4 × 6.0 | 165
| 45HSR2-CT · 230 V | 230 Vac | HSR (High) | 45 | 150 | 215 | T3 | 2 | 12.8 × 6.2 | 172
| 60HSR2-CT · 230 V | 230 Vac | HSR (High) | 60 | 150 | 215 | T3 | 2 | 12.8 × 6.2 | 176
| 30HSR1-CT · 120 V | 120 Vac | HSR (High) | 30 | 150 | 215 | T3 | 2 | 12.4 × 6.0 | 165
Suffix -CR denotes cross-linked polyolefin outer jacket; suffix -CT denotes fluoropolymer outer jacket for chemical and hydrocarbon resistance.

## Max. circuit length & Type C br
Self-Regulating Heat Tracing Cable – Max. circuit length & Type C breaker sizing (230 Vac) (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/self-regulating-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Model designation | Start-up T °C | 16 A Type C max m | 20 A Type C max m | 25 A Type C max m | 32 A Type C max m
10LSR2-CT (10 W/m) | +10 °C | 150 | 185 | 200 | 200
10LSR2-CT (10 W/m) | −20 °C | 102 | 128 | 158 | 182
20LSR2-CT (20 W/m) | +10 °C | 92 | 115 | 135 | 135
20LSR2-CT (20 W/m) | −20 °C | 62 | 78 | 98 | 122
30LSR2-CT (30 W/m) | +10 °C | 64 | 80 | 100 | 110
30MSR2-CT (30 W/m) | +10 °C | 68 | 85 | 106 | 120
45MSR2-CT (45 W/m) | +10 °C | 46 | 58 | 72 | 92
30HSR2-CT (30 W/m) | +10 °C | 72 | 90 | 112 | 135
60HSR2-CT (60 W/m) | +10 °C | 36 | 45 | 56 | 72
Maximum circuit lengths account for cold-start inrush current and a maximum 10 % bus-wire voltage drop under IEC 60364 Type C circuit breakers with 30 mA ground-fault protection.

## Technical data
Self-Regulating Heat Tracing Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/self-regulating-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Linear output | 10–60 W/m @10°C (LSR 10–30 · MSR 15–45 · HSR 15–60 W/m)
Key data | Maintain temp. | Up to +150 °C (LSR +65 °C · MSR +110 °C · HSR +150 °C)
Key data | Max. exposure T | +85 to +215 °C (HSR withstands +215 °C steam purge)
Key data | Supply voltage | 120 / 230 Vac (110–120 V AC and 208–277 V AC grades)
Key data | Bus conductors | 2 × 1.25–2.0 mm² (Stranded tinned or nickel-plated Cu)
Key data | Min. bend radius | 25–35 mm (25 mm at +20 °C · 35 mm at −40 °C)
Electrical | Rated supply voltage | 110–120 Vac (1-er) & 208–277 Vac (2-er)
Electrical | Nominal linear power | 10, 15, 20, 25, 30, 45 & 60 W/m at +10 °C
Electrical | Dielectric withstand | 2.5 kV AC for 1 min (core to earth braid)
Electrical | Earth screen coverage | ≥ 70 % tinned-copper braid (< 18.2 Ω/km)
Thermal | Max. maintain temp. | LSR +65 °C · MSR +110 °C · HSR +150 °C
Thermal | Max. exposure temp. | LSR +85 °C · MSR +135 °C · HSR +215 °C
Thermal | Min. installation T | −40 °C (polyolefin) · −60 °C (fluoropolymer)
Thermal | T-class rating | T6 (+85 °C), T4 (+135 °C) & T3 (+200 °C)
Mechanical | Bus wire cross-section | 1.25 mm² (LSR), 1.5 mm² (MSR), 2.0 mm² (HSR)
Mechanical | Min. bending radius | 25 mm at +20 °C · 35 mm at −40 °C (flat)
Mechanical | Impact & crush class | 2 J impact & 1,500 N crush per IEC 60079-30-1
Mechanical | Field overlapping | Safe for single-overlap on valves & flanges
Resistance | Flame retardance | IEC 60332-1-2 & IEEE 515 vertical flame
Resistance | Chemicals & oils | -CT fluoropolymer resists acids, bases & oils
Resistance | Moisture & ingress | IP66/IP67 when terminated with approved kits
Resistance | UV & weathering | UV-stabilised outer jacket per IEC 60079-30-1
Standards | Design & test standards | IEC/IEEE 60079-30-1, IEC 62395-1 & IEEE 515
Standards | Conductor standard | IEC 60228 Class 2/5 & ASTM B33 / ASTM B355
Standards | Earth fault protection | 30 mA RCD / GFPD required per IEC 60079-30-2
Standards | RoHS & REACH | RoHS 2011/65/EU & REACH compliant compounds
Identification | Series colour coding | Black (LSR) · Brown/Orange (MSR) · Red (HSR)
Identification | Jacket suffix codes | -CR (polyolefin) · -CT (fluoropolymer)
Identification | Surface legend | Model, W/m @ 10 °C, Vac, T-class & metre mark
Identification | Customs tariff (HS) | 8544.49 (or 8516.80 heating resistors)

## Construction
Self-Regulating Heat Tracing Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/self-regulating-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Parallel tinned-copper bus wires | 2 × 1.25 mm² (LSR), 1.5 mm² (MSR) or 2.0 mm² (HSR) stranded tinned / nickel-plated copper bus wires | IEC 60079-30-1 / ASTM B33
2 | Self-regulating PTC conductive polymer core | Radiation-crosslinked carbon-loaded positive temperature coefficient (PTC) heating matrix extruded continuously across the bus wires | IEC 60079-30-1 / IEEE 515
3 | Primary dielectric insulation jacket | Cross-linked polyolefin (LSR/MSR) or high-temperature fluoropolymer (HSR) primary electrical insulation | IEC 60079-30-1
4 | Tinned-copper protective earthing braid | Closely woven tinned-copper wire braid (≥ 70 % optical coverage) providing continuous earth fault path and mechanical protection | IEC 60079-30-1 Clause 4.4
5 | Anti-corrosion outer overjacket | UV-stabilised cross-linked polyolefin (-CR) for aqueous/mild areas or fluoropolymer (-CT) for corrosive chemical and hydrocarbon zones | IEC 60079-30-1 / IEEE 515
| LSR Series · Low Temperature (10–30 W/m @ 10 °C) | Maintain up to +65 °C · Max exposure +85 °C · 1.25 mm² SnCu bus + XLPO insulation + SnCu braid + polyolefin (-CR) or fluoropolymer (-CT) jacket
| MSR Series · Medium Temperature (15–45 W/m @ 10 °C) | Maintain up to +110 °C · Max exposure +135 °C · 1.5 mm² SnCu bus + high-temp XLPO/FEP dielectric + SnCu braid + -CR / -CT outer sheath
| HSR Series · High Temperature (15–60 W/m @ 10 °C) | Maintain up to +150 °C · Steam-purge exposure +215 °C (power off) · 2.0 mm² NiCu/SnCu bus + fluoropolymer dielectric + SnCu braid + fluoropolymer (-CT) sheath

## Quality and supply
Self-Regulating Heat Tracing Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/self-regulating-heat-tracing-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage withstand test — 2.5 kV RMS AC for 1 min between bus conductors and metallic earth braid without breakdown | Every reel
Routine test | Thermal output & calibration verification — Linear power output W/m verified at +10 °C reference pipe temperature within ±10 % tolerance | Every reel
Sample test | Cold impact, crush & mandrel bend test — 2 J mechanical impact and 1,500 N deformation load followed by dielectric verification | Production lot
Type test | Thermal stability & T-class ignition evaluation — Cyclic thermal aging and stabilised sheath temperature verification for T6, T4 and T3 ratings | Type qualification
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · [MODEL] · [W/m] @ 10°C · [120V/230V] · IEC/IEEE 60079-30-1 · [T6/T4/T3] · METRE MARK
Supply | Delivery form: Continuous bulk reels (100 m, 250 m, 500 m) or cut circuits
Supply | Lengths: Field cut-to-length at any point along the parallel bus
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None