## Request a quote
Request a quotation for Series Resistance Heating Cable
Application engineer · industrial heat-tracing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/series-resistance-heating-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Series Resistance Heating Cable – Resistance steps, core geometry & dimensions (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/series-resistance-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Model · Resistance code | Voltage grade | Cores count | Res. @20°C Ω/m | Res. @20°C Ω/km | Conductor alloy / CSA | Max exp. °C | Nominal OD mm | Mass ≈ kg/km
| SRQ-1C-00018 · 10 mm² Cu | 0.6/1 kV | 1C | 0.0018 | 1.8 | NiCu 10 mm² | 260 | 7.8 | 148
| SRQ-1C-00031 · 6.0 mm² Cu | 0.6/1 kV | 1C | 0.0031 | 3.1 | NiCu 6.0 mm² | 260 | 6.6 | 102
| SRQ-1C-00046 · 4.0 mm² Cu | 0.6/1 kV | 1C | 0.0046 | 4.6 | NiCu 4.0 mm² | 260 | 5.8 | 76
| SRQ-1C-00074 · 2.5 mm² Cu | 450/750 V | 1C | 0.0074 | 7.4 | NiCu 2.5 mm² | 260 | 5.2 | 58
| SRQ-1C-0012 · 1.5 mm² Cu | 450/750 V | 1C | 0.0121 | 12.1 | NiCu 1.5 mm² | 260 | 4.7 | 45
| SRQ-1C-0025 · CuNi Alloy | 450/750 V | 1C | 0.025 | 25 | CuNi2 2.5 mm² | 260 | 5.2 | 57
| SRQ-1C-0050 · CuNi Alloy | 450/750 V | 1C | 0.05 | 50 | CuNi6 2.0 mm² | 260 | 5 | 52
| SRQ-1C-0100 · CuNi Alloy | 450/750 V | 1C | 0.1 | 100 | CuNi10 1.5 mm² | 260 | 4.7 | 46
| SRQ-1C-0250 · CuNi23 Alloy | 450/750 V | 1C | 0.25 | 250 | CuNi23 1.5 mm² | 260 | 4.7 | 45
| SRQ-1C-0500 · CuNi44 Alloy | 450/750 V | 1C | 0.5 | 500 | CuNi44 1.0 mm² | 260 | 4.4 | 39
| SRQ-1C-1000 · NiCr Alloy | 450/750 V | 1C | 1 | 1000 | NiCr 1.1 mm² | 260 | 4.5 | 40
| SRQ-1C-1800 · NiCr Alloy | 450/750 V | 1C | 1.8 | 1800 | NiCr 0.6 mm² | 260 | 4.2 | 34
| SRQ-2C-0015 · Twin Loop | 450/750 V | 2C | 0.0148 | 14.8 | 2×2.5 mm² NiCu | 260 | 8.6 | 118
| SRQ-2C-0200 · Twin Loop | 450/750 V | 2C | 0.2 | 200 | 2×1.5 mm² CuNi | 260 | 8 | 96
| SRQ-3C-00031 · 3-Phase Star | 0.6/1 kV | 3C | 0.0031 | 3.1 | 3×6.0 mm² NiCu | 260 | 12.8 | 310
| SRQ-3C-00074 · 3-Phase Star | 0.6/1 kV | 3C | 0.0074 | 7.4 | 3×2.5 mm² NiCu | 260 | 10.2 | 175
For 2C twin-core cables, resistance values represent loop resistance per metre of cable; for 3C three-phase cables, resistance is stated per core per metre.

## Typical single-feed pipeline ci
Series Resistance Heating Cable – Typical single-feed pipeline circuit lengths (400 V & 690 V 3-phase star) (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/series-resistance-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Cable configuration | Core res. Ω/km | 400V @ 15 W/m circuit m | 400V @ 25 W/m circuit m | 690V @ 15 W/m circuit m | 690V @ 25 W/m circuit m
3 × SRQ-1C-00018 (10 mm² Cu) | 1.8 | 2430 | 1880 | 3500 | 3240
SRQ-3C-00031 (3×6.0 mm² Cu) | 3.1 | 1850 | 1430 | 3190 | 2470
3 × SRQ-1C-00046 (4.0 mm² Cu) | 4.6 | 1520 | 1180 | 2620 | 2030
SRQ-3C-00074 (3×2.5 mm² Cu) | 7.4 | 1200 | 930 | 2070 | 1600
3 × SRQ-1C-0012 (1.5 mm² Cu) | 12.1 | 940 | 725 | 1620 | 1250
3 × SRQ-1C-0050 (CuNi6 Alloy) | 50 | 460 | 355 | 795 | 615
Three-phase star (wye) connection at the far end of the pipeline balances phase currents and eliminates a separate return power cable.

## Technical data
Series Resistance Heating Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/series-resistance-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Resistance range | 0.0018–1.8 Ω/m (1.8 to 1,800 Ω/km @ 20 °C (±5 %))
Key data | Circuit length | 200–3,500 m (Single power feed for long pipelines)
Key data | Max. exposure T | +260 °C (Maintain up to +200 °C · Exp. +260 °C)
Key data | Rated voltage | 450/750–1000 V (230 V, 400 V, 480 V, 600 V & 690 V)
Key data | Linear output | Up to 40 W/m (Custom W/m = I² × R along full length)
Key data | Min. bend radius | 5 × OD (Concentric round or flat twin/3-core)
Electrical | Rated voltage grade | 450/750 V & 0.6/1 kV (up to 600/690 Vac)
Electrical | Conductor resistance | 0.0018 to 1.8 Ω/m (1.8–1,800 Ω/km @ 20 °C)
Electrical | Resistance tolerance | ±5 % (alloys) or per IEC 60228 Class 2/5 Cu
Electrical | Dielectric withstand | 2.5 kV to 3.5 kV AC for 1 min (core-to-braid)
Thermal | Max. exposure temp. | +260 °C continuous (PTFE / PFA fluoropolymer)
Thermal | Max. maintain temp. | Up to +200 °C (depending on W/m & T-class)
Thermal | Max. linear output | Up to 30–40 W/m (circuit-specific design)
Thermal | Min. installation T | −60 °C (fluoropolymer PTFE / PFA jacket)
Mechanical | Core configurations | Single-core (1C), twin (2C) & 3-core (3C)
Mechanical | Min. bending radius | 5 × OD (or 25 mm minimum, fixed routing)
Mechanical | Impact & crush test | 7 J / 2 J impact & 1,500 N deformation load
Mechanical | Length alteration | Do not cut to length; cutting alters Ω & W/m
Resistance | Flame retardance | IEC 60332-1-2 & UL VW-1 flame retardant
Resistance | Chemicals & oils | Inert to acids, alkalis, solvents & sour oil
Resistance | Steam-purge resilience | Withstands +260 °C saturated steam purging
Resistance | Moisture & UV | Non-hygroscopic (< 0.01 %) & UV immune
Standards | Applicable standards | IEC/IEEE 60079-30-1, IEC 62395-1 & IEEE 515
Standards | System design standard | IEC/IEEE 60079-30-2 & IEEE 515 design guide
Standards | Earth fault device | 30 mA RCD / GFPD required per IEC 60079-30-2
Standards | RoHS & REACH | RoHS 2011/65/EU & REACH compliant materials
Identification | Resistance code print | Nominal Ω/km or Ω/m at +20 °C on outer sheath
Identification | Core identification | 1C: Natural/Red · 2C: Bk/Rd · 3C: Bk/Rd/Bu
Identification | Outer sheath colour | Red, Blue or Black PFA / FEP with metre marks
Identification | Customs tariff (HS) | 8544.49 (or 8516.80 electric heating cables)

## Construction
Series Resistance Heating Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/series-resistance-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Calibrated series resistance conductor(s) | 1, 2 or 3 stranded conductors in nickel-plated copper (1.5–16 mm²) or CuNi / NiCr resistance alloys (0.0018 to 1.8 Ω/m at 20 °C) | IEC 60079-30-1 / IEEE 515
2 | PTFE / PFA fluoropolymer core insulation | Heavy-wall PTFE or melt-extruded PFA primary dielectric rated for 450/750 V (0.6/1 kV grade) and +260 °C continuous exposure | IEC 60079-30-1
3 | PTFE / glass-fibre thermal bedding tape | Lapped PTFE/fibreglass binder tape equalising radial thermal flux and cushioning the core assembly | IEC 60079-30-1
4 | Tinned / nickel-plated copper earth braid | Closely woven tinned or nickel-plated copper wire braid (≥ 70 % optical coverage) providing continuous protective earthing | IEC 60079-30-1 Clause 4.4
5 | Extruded PFA / FEP fluoropolymer outer sheath | Pinhole-free extruded perfluoroalkoxy (PFA) or FEP outer jacket resistant to +260 °C steam purge, hydrocarbons and corrosive chemicals | IEC 60079-30-1 / IEEE 515
| 1C Series · Single-Core Loop / 3-Phase Star (0.0018–1.8 Ω/m) | 450/750 V & 0.6/1 kV · +260 °C · Single resistance core + PTFE/PFA wall + SnCu braid + PFA outer sheath for 3×1C balanced 3-phase pipelines
| 2C Series · Twin-Core Single-End Return (0.007–1.8 Ω/m) | 450/750 V · +260 °C · Twin resistance cores looped at the far end so power supply and termination remain at one end of the pipe
| 3C Series · Three-Core Balanced 3-Phase (0.0018–0.50 Ω/m) | 450/750 V & 0.6/1 kV · +260 °C · Three star-connected resistance cores in one jacket for single-feed 400–690 V pipelines up to 3,500 m

## Quality and supply
Series Resistance Heating Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/series-resistance-heating-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC/IEEE 60079-30-1 & IEEE 515. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric voltage withstand test — 2.5 kV to 3.5 kV RMS AC for 1 min (2U + 1,000 V) between resistance cores and earth braid | Every circuit / reel
Routine test | Calibrated DC conductor resistance check — DC resistance per metre verified at +20 °C within ±5 % tolerance across each core | Every circuit / reel
Sample test | 260 °C fluoropolymer thermal aging & cold bend — Thermal endurance at +260 °C and −60 °C cold mandrel bend test without cracking | Production lot
Sample test | Mechanical impact & crush deformation test — Impact and 1,500 N crush verification followed by immersed dielectric withstand test | Production lot
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · [SRQ MODEL] · [Ω/km @ 20°C] · [450/750V or 0.6/1kV] · PTFE/PFA +260°C · IEC 60079-30-1 · METRE MARK
Supply | Delivery form: Engineered factory-terminated circuits or bulk reels
Supply | Lengths: Custom circuit lengths from 200 m to 3,500 m per feed
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None