## Request a quote
Request a quotation for SiFCuSi
Application engineer · high-temperature, ignition & UHV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/sifcusi-copper-braid-screened-silicone-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SiFCuSi Copper-Braid Screened Silicone Cable – Dimensions & weights (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sifcusi-copper-braid-screened-silicone-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section / size | Conductor build | Wall ≈ mm | Outer Ø ≈ mm | Metal kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| SiFCuSi 1×0.5 | 1×0.5 | Class 5 Sn-Cu (0.5 mm²) | 1.5 | 5 | 23.8 | 51.3 | 25 | Standard SiFCuSi configurations
| SiFCuSi 1×0.75 | 1×0.75 | Class 5 Sn-Cu (0.75 mm²) | 1.5 | 5.3 | 27.3 | 58.2 | 26 | Standard SiFCuSi configurations
| SiFCuSi 1×1 | 1×1 | Class 5 Sn-Cu (1 mm²) | 1.5 | 5.4 | 30.1 | 62.2 | 27 | Standard SiFCuSi configurations
| SiFCuSi 1×1.5 | 1×1.5 | Class 5 Sn-Cu (1.5 mm²) | 1.5 | 5.7 | 36.1 | 71.8 | 28 | Standard SiFCuSi configurations
| SiFCuSi 1×2.5 | 1×2.5 | Class 5 Sn-Cu (2.5 mm²) | 1.5 | 6.6 | 49.1 | 97 | 33 | Standard SiFCuSi configurations
| SiFCuSi 1×4 | 1×4 | Class 5 Sn-Cu (4 mm²) | 1.9 | 8 | 68.8 | 139.2 | 40 | Standard SiFCuSi configurations
| SiFCuSi 1×6 | 1×6 | Class 5 Sn-Cu (6 mm²) | 1.9 | 8.6 | 90.3 | 171.7 | 43 | Standard SiFCuSi configurations
| SiFCuSi 1×10 | 1×10 | Class 5 Sn-Cu (10 mm²) | 1.9 | 9.9 | 133.6 | 241.4 | 50 | Standard SiFCuSi configurations
| SiFCuSi 1×16 | 1×16 | Class 5 Sn-Cu (16 mm²) | 1.9 | 11 | 195.4 | 328.5 | 55 | Standard SiFCuSi configurations
| SiFCuSi 1×25 | 1×25 | Class 5 Sn-Cu (25 mm²) | 1.9 | 12.4 | 287.1 | 456.2 | 62 | Standard SiFCuSi configurations
| SiFCuSi 2×0.75 | 2×0.75 | Class 5 Sn-Cu (0.75 mm²) | 1.5 | 7.6 | 43.3 | 106.8 | 46 | Standard SiFCuSi configurations
| SiFCuSi 3G1.5 | 3G1.5 | Class 5 Sn-Cu (1.5 mm²) | 1.5 | 9 | 77.4 | 166.5 | 54 | Standard SiFCuSi configurations
| SiFCuSi 4G1.5 | 4G1.5 | Class 5 Sn-Cu (1.5 mm²) | 1.5 | 9.8 | 94.8 | 200.4 | 59 | Standard SiFCuSi configurations
| SiFCuSi 4G2.5 | 4G2.5 | Class 5 Sn-Cu (2.5 mm²) | 1.5 | 11.9 | 141.2 | 297 | 71 | Standard SiFCuSi configurations
Outer diameters and weights are nominal engineering values for SiFCuSi subject to standard manufacturing tolerances per DIN VDE 0250-1 / EN 50525-2-83.

## Electrical & rating data
SiFCuSi Copper-Braid Screened Silicone Cable – Electrical & rating data (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sifcusi-copper-braid-screened-silicone-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Primary rating (A or kV) | Derated / AC rating | Dielectric test V AC rms
1×0.5 mm² | 40.1 | 9 | 7 | 2000
1×0.75 mm² | 26.7 | 12 | 9 | 2000
1×1 mm² | 20 | 15 | 12 | 2000
1×1.5 mm² | 13.7 | 18 | 14 | 2000
1×2.5 mm² | 8.21 | 26 | 20 | 2000
1×4 mm² | 5.09 | 34 | 27 | 2000
1×6 mm² | 3.39 | 44 | 34 | 2000
1×10 mm² | 1.95 | 61 | 48 | 2000
1×16 mm² | 1.24 | 82 | 64 | 2000
1×25 mm² | 0.795 | 108 | 84 | 2000
2×0.75 mm² | 26.7 | 12 | 9 | 2000
3G1.5 mm² | 13.7 | 18 | 14 | 2000
4G1.5 mm² | 13.7 | 18 | 14 | 2000
4G2.5 mm² | 8.21 | 26 | 20 | 2000
Electrical resistance at +20 °C and dielectric withstand voltages verified per DIN VDE 0250-1 / EN 50525-2-83.

## Technical data
SiFCuSi Copper-Braid Screened Silicone Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/sifcusi-copper-braid-screened-silicone-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (U0/U · 2000 V AC test voltage)
Key data | Temperature | -60…+180 °C (Continuous · +200 °C short-term)
Key data | Conductor | Sn-Cu Class 5 (Fine-stranded tinned copper)
Key data | Architecture | Si + Cu + Si (Inner Si + Cu braid + outer Si)
Key data | Min bend radius | 5 × OD fixed (12 × OD flexing installation)
Key data | Size range | 0.5 to 25 mm² (Single-core & screened multicore)
Electrical | Rated voltage U0/U | 300/500 V AC
Electrical | AC test voltage (core/screen) | 2000 V AC (50 Hz, 5 min)
Electrical | AC test voltage (screen/water) | 1000 V AC on outer silicone sheath
Electrical | Insulation resistance | ≥ 200 MΩ·km at +20 °C
Electrical | Screen optical coverage | ≥ 85 % tinned copper braid
Thermal | Operating temperature range | -60 °C to +180 °C continuous
Thermal | Short-term peak temperature | +200 °C to +220 °C
Thermal | Short-circuit conductor temp. | +250 °C
Thermal | Cryogenic flexibility limit | Remains flexible down to -60 °C
Mechanical | Conductor stranding | IEC 60228 Class 5 fine-stranded tinned Cu
Mechanical | Min. bending radius (fixed) | 5 × overall cable diameter
Mechanical | Min. bending radius (flexing) | 12 × overall cable diameter
Resistance | Flame retardance | IEC 60332-1-2 self-extinguishing
Resistance | Halogen-free & acid gas | IEC 60754-1 & IEC 60754-2
Resistance | Smoke density | IEC 61034-2 low smoke emission
Resistance | Weather, UV & ozone | Immune to ozone cracking and UV ageing
Standards | Design standard | DIN VDE 0250-1 / EN 50525-2-83 ref.
Standards | Conductor standard | IEC 60228 Class 5 tinned copper
Standards | RoHS & REACH | RoHS 3 & REACH compliant
Identification | Outer jacket colour | Red-brown (optional white or black)
Identification | Surface legend | TEBAOFLEX SiFCuSi [size] 300/500 V +180 °C
Identification | Customs tariff (HS) | 8544.49

## Construction
SiFCuSi Copper-Braid Screened Silicone Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/sifcusi-copper-braid-screened-silicone-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 tinned copper conductor | Fine-stranded tinned electrolytic copper (IEC 60228 Class 5)
2 | Inner silicone dielectric (Si) | Cross-linked silicone rubber Type EI2 (EN 50363-1)
3 | Concentric tinned copper braid (Cu) | Braided tinned copper wires (≥ 85 % optical coverage)
4 | Outer silicone rubber jacket (Si) | Extruded halogen-free silicone elastomer outer sheath (red-brown)
| SiFCuSi 1× (0.5–25 mm²) | Coaxial-style single-core screened silicone hook-up and motor lead wire
| SiFCuSi Multi (2×–5G) | Screened paired and multicore silicone sensor/control assemblies

## Quality and supply
SiFCuSi Copper-Braid Screened Silicone Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/sifcusi-copper-braid-screened-silicone-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Dielectric spark / high-voltage withstand test — 100 % in-line spark and AC/DC dielectric withstand per DIN VDE 0250-1 / EN 50525-2-83 | Every manufactured length
Routine test | Conductor DC resistance & continuity check — Within maximum 20 °C resistance limit specified for SiFCuSi | Every spool or drum length
Sample test | Thermal ageing & dimensional verification — Wall thickness, concentricity and post-ageing elongation per DIN VDE 0250-1 / EN 50525-2-83 | Per production batch
Type test | Flame, outgassing or high-temperature endurance — Qualified to DIN VDE 0250-1 / EN 50525-2-83 thermal and environmental performance criteria | Type qualification
Standard / approval | DIN VDE 0250-1 / EN 50525-2-83
Standard / approval | CE (2014/35/EU) & RoHS 3 (2015/863/EU) Compliant
Standard / approval | REACH SVHC & Halogen/Asbestos Compliance Verified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX SiFCuSi 1×2.5 300/500 V -60/+180 °C CE
Supply | Delivery form: Precision spools, coils or export wooden drums
Supply | Standard lengths: 50 m · 100 m · 500 m · 1000 m (or cut harnesses)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP