## Request a quote
Request a quotation for SiHFC
Application engineer · high-temperature, ignition & UHV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/sihfc-screened-multicore-silicone-high-temperature-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
SiHFC Screened Multicore Silicone High-Temperature Cable – Dimensions & weights (20)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sihfc-screened-multicore-silicone-high-temperature-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section / size | Conductor build | Wall ≈ mm | Outer Ø ≈ mm | Metal kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| SiHFC 2×0.75 | 2×0.75 | Class 5 Sn-Cu (0.75 mm²) | 1.5 | 7.6 | 43.3 | 106.8 | 46 | Standard SiHFC configurations
| SiHFC 3G0.75 | 3G0.75 | Class 5 Sn-Cu (0.75 mm²) | 1.5 | 8 | 52 | 122.4 | 48 | Standard SiHFC configurations
| SiHFC 4G0.75 | 4G0.75 | Class 5 Sn-Cu (0.75 mm²) | 1.5 | 8.6 | 61.5 | 142.9 | 52 | Standard SiHFC configurations
| SiHFC 5G0.75 | 5G0.75 | Class 5 Sn-Cu (0.75 mm²) | 1.5 | 9.3 | 71.3 | 166.4 | 56 | Standard SiHFC configurations
| SiHFC 7G0.75 | 7G0.75 | Class 5 Sn-Cu (0.75 mm²) | 1.5 | 10 | 88.4 | 198.4 | 60 | Standard SiHFC configurations
| SiHFC 2×1 | 2×1 | Class 5 Sn-Cu (1 mm²) | 1.5 | 8 | 49.6 | 120 | 48 | Standard SiHFC configurations
| SiHFC 3G1 | 3G1 | Class 5 Sn-Cu (1 mm²) | 1.5 | 8.4 | 60.7 | 138.3 | 50 | Standard SiHFC configurations
| SiHFC 4G1 | 4G1 | Class 5 Sn-Cu (1 mm²) | 1.5 | 9 | 72.6 | 161.7 | 54 | Standard SiHFC configurations
| SiHFC 5G1 | 5G1 | Class 5 Sn-Cu (1 mm²) | 1.5 | 9.7 | 84.9 | 188.4 | 58 | Standard SiHFC configurations
| SiHFC 2×1.5 | 2×1.5 | Class 5 Sn-Cu (1.5 mm²) | 1.5 | 8.6 | 61.5 | 142.9 | 52 | Standard SiHFC configurations
| SiHFC 3G1.5 | 3G1.5 | Class 5 Sn-Cu (1.5 mm²) | 1.5 | 9 | 77.4 | 166.5 | 54 | Standard SiHFC configurations
| SiHFC 4G1.5 | 4G1.5 | Class 5 Sn-Cu (1.5 mm²) | 1.5 | 9.8 | 94.8 | 200.4 | 59 | Standard SiHFC configurations
| SiHFC 5G1.5 | 5G1.5 | Class 5 Sn-Cu (1.5 mm²) | 1.5 | 10.5 | 111.9 | 233.2 | 63 | Standard SiHFC configurations
| SiHFC 7G1.5 | 7G1.5 | Class 5 Sn-Cu (1.5 mm²) | 1.5 | 11.4 | 144.1 | 287.1 | 68 | Standard SiHFC configurations
| SiHFC 12G1.5 | 12G1.5 | Class 5 Sn-Cu (1.5 mm²) | 1.5 | 14.7 | 228.7 | 466.4 | 88 | Standard SiHFC configurations
| SiHFC 3G2.5 | 3G2.5 | Class 5 Sn-Cu (2.5 mm²) | 1.5 | 10.9 | 113.4 | 244.1 | 65 | Standard SiHFC configurations
| SiHFC 4G2.5 | 4G2.5 | Class 5 Sn-Cu (2.5 mm²) | 1.5 | 11.9 | 141.2 | 297 | 71 | Standard SiHFC configurations
| SiHFC 5G2.5 | 5G2.5 | Class 5 Sn-Cu (2.5 mm²) | 1.5 | 12.9 | 169 | 352.1 | 77 | Standard SiHFC configurations
| SiHFC 4G4 | 4G4 | Class 5 Sn-Cu (4 mm²) | 1.9 | 14 | 206.8 | 422.4 | 84 | Standard SiHFC configurations
| SiHFC 4G6 | 4G6 | Class 5 Sn-Cu (6 mm²) | 1.9 | 15.5 | 289.3 | 553.6 | 93 | Standard SiHFC configurations
Outer diameters and weights are nominal engineering values for SiHFC subject to standard manufacturing tolerances per DIN VDE 0250-1 / EN 50525-2-83.

## Electrical & rating data
SiHFC Screened Multicore Silicone High-Temperature Cable – Electrical & rating data (20)
TEBAOFLEX ¦ https://tebaoflex.com/cables/sihfc-screened-multicore-silicone-high-temperature-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Primary rating (A or kV) | Derated / AC rating | Dielectric test V AC rms
2×0.75 mm² | 26.7 | 12 | 9 | 2000
3G0.75 mm² | 26.7 | 12 | 9 | 2000
4G0.75 mm² | 26.7 | 12 | 9 | 2000
5G0.75 mm² | 26.7 | 12 | 9 | 2000
7G0.75 mm² | 26.7 | 12 | 9 | 2000
2×1 mm² | 20 | 15 | 12 | 2000
3G1 mm² | 20 | 15 | 12 | 2000
4G1 mm² | 20 | 15 | 12 | 2000
5G1 mm² | 20 | 15 | 12 | 2000
2×1.5 mm² | 13.7 | 18 | 14 | 2000
3G1.5 mm² | 13.7 | 18 | 14 | 2000
4G1.5 mm² | 13.7 | 18 | 14 | 2000
5G1.5 mm² | 13.7 | 18 | 14 | 2000
7G1.5 mm² | 13.7 | 18 | 14 | 2000
12G1.5 mm² | 13.7 | 18 | 14 | 2000
3G2.5 mm² | 8.21 | 26 | 20 | 2000
4G2.5 mm² | 8.21 | 26 | 20 | 2000
5G2.5 mm² | 8.21 | 26 | 20 | 2000
4G4 mm² | 5.09 | 34 | 27 | 2000
4G6 mm² | 3.39 | 44 | 34 | 2000
Electrical resistance at +20 °C and dielectric withstand voltages verified per DIN VDE 0250-1 / EN 50525-2-83.

## Technical data
SiHFC Screened Multicore Silicone High-Temperature Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/sihfc-screened-multicore-silicone-high-temperature-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (U0/U · 2000 V AC test voltage)
Key data | Temperature | -60…+180 °C (Continuous · +220 °C short-term)
Key data | Conductor | Sn-Cu Class 5 (Fine-stranded tinned copper)
Key data | EMC screen | Sn-Cu braid (≥ 85 % optical coverage shield)
Key data | Min bend radius | 6 × OD fixed (15 × OD occasional flexing)
Key data | Core range | 2 to 12 cores (0.75 to 6.0 mm² multicore range)
Electrical | Rated voltage U0/U | 300/500 V AC
Electrical | AC test voltage (core/core) | 2000 V AC (50 Hz, 5 min)
Electrical | AC test voltage (core/screen) | 2000 V AC
Electrical | Specific insulation resistance | ≥ 200 MΩ·km at +20 °C
Electrical | EMC braid optical coverage | ≥ 85 % tinned copper wire braid
Thermal | Operating temperature (fixed) | -60 °C to +180 °C
Thermal | Short-term peak temperature | +220 °C (intermittent thermal excursion)
Thermal | Min. flexing installation temp. | -25 °C
Thermal | Combustion silica ash integrity | Forms non-conductive SiO2 ash in fire
Mechanical | Conductor stranding | IEC 60228 Class 5 fine-stranded tinned Cu
Mechanical | Min. bending radius (fixed) | 6 × overall cable diameter
Mechanical | Min. bending radius (flexing) | 15 × overall cable diameter
Mechanical | Ventilation requirement | Keep well-ventilated above +100 °C
Resistance | Flame retardance | IEC 60332-1-2 vertical flame test
Resistance | Halogen-free & acid gas | IEC 60754-1 & IEC 60754-2 (0 % halogens)
Resistance | Smoke density | Low smoke emission per IEC 61034-2
Resistance | Chemical & oil resistance | Resists animal/vegetable oils, ozone & UV
Standards | Reference standard | DIN VDE 0250-1 / EN 50525-2-83 based
Standards | Core identification | DIN VDE 0293-308 (≤ 5 cores) or numbered
Standards | RoHS & REACH | RoHS 3 & REACH SVHC compliant
Identification | Outer sheath colour | Red-brown (RAL 3011 / oxide red)
Identification | Sheath marking | TEBAOFLEX SiHFC [n×mm²] 300/500 V +180 °C
Identification | Customs tariff (HS) | 8544.49

## Construction
SiHFC Screened Multicore Silicone High-Temperature Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/sihfc-screened-multicore-silicone-high-temperature-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Fine-stranded tinned copper | Tinned annealed electrolytic copper (IEC 60228 Class 5)
2 | Silicone core insulation | Cross-linked silicone rubber compound Type EI2 (EN 50363-1)
3 | Core wrapping tape | Heat-resistant polyester / glass-fleece separator tape over cabled cores
4 | Tinned copper EMC braid | Interwoven tinned copper wire braid (≥ 85 % optical coverage)
5 | Outer silicone rubber sheath | Halogen-free cross-linked silicone elastomer (red-brown)
| SiHFC-J (3G–12G) | Colour-coded or black numbered cores including green-yellow protective earth conductor
| SiHFC-O (2×–7×) | Without green-yellow conductor for isolated thermocouple extension, RTD, and control circuits

## Quality and supply
SiHFC Screened Multicore Silicone High-Temperature Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/sihfc-screened-multicore-silicone-high-temperature-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250-1 / EN 50525-2-83. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Dielectric spark / high-voltage withstand test — 100 % in-line spark and AC/DC dielectric withstand per DIN VDE 0250-1 / EN 50525-2-83 | Every manufactured length
Routine test | Conductor DC resistance & continuity check — Within maximum 20 °C resistance limit specified for SiHFC | Every spool or drum length
Sample test | Thermal ageing & dimensional verification — Wall thickness, concentricity and post-ageing elongation per DIN VDE 0250-1 / EN 50525-2-83 | Per production batch
Type test | Flame, outgassing or high-temperature endurance — Qualified to DIN VDE 0250-1 / EN 50525-2-83 thermal and environmental performance criteria | Type qualification
Standard / approval | DIN VDE 0250-1 / EN 50525-2-83
Standard / approval | CE (2014/35/EU) & RoHS 3 (2015/863/EU) Compliant
Standard / approval | REACH SVHC & Halogen/Asbestos Compliance Verified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX SiHFC 4G1.5 300/500 V -60/+180 °C CE
Supply | Delivery form: Precision spools, coils or export wooden drums
Supply | Standard lengths: 50 m · 100 m · 500 m · 1000 m (or cut harnesses)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP