## Request a quote
Request a quotation for Silicone ESD Cleanroom Control Cable
Application engineer · control, railway, mining & tactical cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/besilen-silicone-esd-protected-cleanroom-control-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
Silicone ESD-Protected Cleanroom Control Cable – Dimensions & weights (19)
TEBAOFLEX ¦ https://tebaoflex.com/cables/besilen-silicone-esd-protected-cleanroom-control-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section / size | Conductor build | Wall ≈ mm | Outer Ø ≈ mm | Metal kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| Silicone ESD 2×0.25 | 2×0.25 mm² | Class 5/6 Sn-Cu (0.25 mm²) | 0.9 | 4.9 | 4.8 | 30.7 | 49 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 4×0.25 | 4×0.25 mm² | Class 5/6 Sn-Cu (0.25 mm²) | 0.9 | 5.6 | 9.6 | 43.5 | 56 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 8×0.25 | 8×0.25 mm² | Class 5/6 Sn-Cu (0.25 mm²) | 0.9 | 7 | 19.2 | 72.1 | 70 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 2×0.5 | 2×0.5 mm² | Class 5/6 Sn-Cu (0.5 mm²) | 0.9 | 5.5 | 9.6 | 42.3 | 55 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 4×0.5 | 4×0.5 mm² | Class 5/6 Sn-Cu (0.5 mm²) | 0.9 | 6.3 | 19.2 | 62.1 | 63 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 7G0.5 | 7G0.5 mm² | Class 5/6 Sn-Cu (0.5 mm²) | 0.9 | 7.3 | 33.6 | 91.2 | 73 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 12G0.5 | 12G0.5 mm² | Class 5/6 Sn-Cu (0.5 mm²) | 1.1 | 9.9 | 57.6 | 163.5 | 99 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 3G0.75 | 3G0.75 mm² | Class 5/6 Sn-Cu (0.75 mm²) | 0.9 | 6.2 | 21.6 | 63.1 | 62 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 4G0.75 | 4G0.75 mm² | Class 5/6 Sn-Cu (0.75 mm²) | 0.9 | 6.8 | 28.8 | 78.7 | 68 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 7G0.75 | 7G0.75 mm² | Class 5/6 Sn-Cu (0.75 mm²) | 0.9 | 8 | 50.4 | 119.5 | 80 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 12G0.75 | 12G0.75 mm² | Class 5/6 Sn-Cu (0.75 mm²) | 1.1 | 10.7 | 86.4 | 210 | 107 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 3G1 | 3G1 mm² | Class 5/6 Sn-Cu (1 mm²) | 0.9 | 6.6 | 28.8 | 75.8 | 66 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 4G1 | 4G1 mm² | Class 5/6 Sn-Cu (1 mm²) | 0.9 | 7.2 | 38.4 | 94.4 | 72 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 7G1 | 7G1 mm² | Class 5/6 Sn-Cu (1 mm²) | 0.9 | 8.5 | 67.2 | 145.2 | 85 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 12G1 | 12G1 mm² | Class 5/6 Sn-Cu (1 mm²) | 1.1 | 11.5 | 115.2 | 258 | 115 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 3G1.5 | 3G1.5 mm² | Class 5/6 Sn-Cu (1.5 mm²) | 0.9 | 7.7 | 43.2 | 107.2 | 77 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 4G1.5 | 4G1.5 mm² | Class 5/6 Sn-Cu (1.5 mm²) | 0.9 | 8.4 | 57.6 | 133.8 | 84 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 7G1.5 | 7G1.5 mm² | Class 5/6 Sn-Cu (1.5 mm²) | 0.9 | 10 | 100.8 | 208.8 | 100 | Standard Silicone ESD Cleanroom Control Cable configurations
| Silicone ESD 12G1.5 | 12G1.5 mm² | Class 5/6 Sn-Cu (1.5 mm²) | 1.1 | 13.6 | 172.8 | 372.6 | 136 | Standard Silicone ESD Cleanroom Control Cable configurations
Outer diameters and weights are nominal engineering values for Silicone ESD Cleanroom Control Cable subject to standard manufacturing tolerances per DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone.

## Electrical & rating data
Silicone ESD-Protected Cleanroom Control Cable – Electrical & rating data (19)
TEBAOFLEX ¦ https://tebaoflex.com/cables/besilen-silicone-esd-protected-cleanroom-control-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Primary rating (A or nF/km) | Secondary rating | Dielectric test V AC rms
2×0.25 mm² | 79 | 4 | 3 | 2000
4×0.25 mm² | 79 | 4 | 3 | 2000
8×0.25 mm² | 79 | 4 | 3 | 2000
2×0.5 mm² | 39 | 9 | 7 | 2000
4×0.5 mm² | 39 | 9 | 7 | 2000
7G0.5 mm² | 39 | 9 | 7 | 2000
12G0.5 mm² | 39 | 9 | 7 | 2000
3G0.75 mm² | 26 | 12 | 9 | 2000
4G0.75 mm² | 26 | 12 | 9 | 2000
7G0.75 mm² | 26 | 12 | 9 | 2000
12G0.75 mm² | 26 | 12 | 9 | 2000
3G1 mm² | 19.5 | 15 | 11 | 2000
4G1 mm² | 19.5 | 15 | 11 | 2000
7G1 mm² | 19.5 | 15 | 11 | 2000
12G1 mm² | 19.5 | 15 | 11 | 2000
3G1.5 mm² | 13.3 | 18 | 14 | 2000
4G1.5 mm² | 13.3 | 18 | 14 | 2000
7G1.5 mm² | 13.3 | 18 | 14 | 2000
12G1.5 mm² | 13.3 | 18 | 14 | 2000
Electrical resistance at +20 °C and dielectric withstand voltages verified per DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone.

## Technical data
Silicone ESD-Protected Cleanroom Control Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/besilen-silicone-esd-protected-cleanroom-control-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Surface resist. | 10⁴–10⁷ Ω (ESD dissipative (EN 61340-5-1))
Key data | Cleanroom class | ISO Class 1 (Low-particulate & low-outgassing)
Key data | Rated voltage | 300/500 V (2000 V AC dielectric test)
Key data | Service temp. | -40…+180 °C (High-temp silicone elastomer)
Key data | Conductor | Sn-Cu Class 5/6 (Fine or extra-fine tinned Cu)
Key data | Halogen-free | IEC 60754-1/2 (Non-corrosive & flame-retardant)
Electrical | ESD surface resistance | 10⁴ to 10⁷ Ω (dissipative per EN 61340-5-1)
Electrical | Rated voltage U0/U | 300/500 V AC (up to 0.5 mm²: 300/300 V)
Electrical | AC dielectric test voltage | 2,000 V AC (core-to-core)
Electrical | Core insulation resistance | ≥ 200 MΩ·km at +20 °C
Thermal | Operating temperature (fixed) | -40 °C to +180 °C (short-term +200 °C)
Thermal | Flexing temperature range | -25 °C to +180 °C
Mechanical | Cleanroom classification | ISO 14644-1 Air Cleanliness Class 1
Mechanical | Min. bending radius (flexing) | 10 × overall cable diameter
Mechanical | Min. bending radius (fixed) | 4 × overall cable diameter
Mechanical | Talc-free construction | 100 % chalk- and talc-free for cleanrooms
Resistance | Halogen-free & low smoke | IEC 60754-1/2 & IEC 61034-1/2 pass
Resistance | Flame retardance | IEC 60332-1-2 self-extinguishing
Resistance | Cleanroom wipe resistance | Resists IPA (isopropanol), H₂O₂ & steam
Standards | ESD protection standard | DIN EN 61340-5-1 (EPA compliant)
Standards | Cleanroom qualification | ISO 14644-1 Class 1 (Fraunhofer IPA)
Standards | RoHS & REACH | RoHS 3, REACH & LABS/PWIS-controlled
Identification | Outer sheath colour | Jet black (conductive/dissipative ESD)
Identification | Surface legend | TEBAOFLEX Silicone ESD CLEANROOM [n×mm²] EN 61340-5-1
Identification | Customs tariff (HS) | 8544.49

## Construction
Silicone ESD-Protected Cleanroom Control Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/besilen-silicone-esd-protected-cleanroom-control-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Tinned copper conductors | Fine-stranded or extra-fine-stranded tinned copper wire (IEC 60228 Class 5 / Class 6)
2 | Silicone EI2 silicone insulation | High-purity cross-linked silicone elastomer (colour-coded per DIN 47100 or numbered + GNYE)
3 | Antistatic ESD silicone outer jacket | Volume-conductive carbon-modified cross-linked silicone elastomer (jet black, R_surface 10⁴–10⁷ Ω)
| Silicone ESD Unscreened (2×0.25–18G1.5) | Antistatic silicone cleanroom control and sensor cable with 10⁴–10⁷ Ω dissipative outer sheath
| Silicone ESD-C Screened (2×0.25–12G1.5) | EMC tinned-copper-braid screened + antistatic ESD outer sheath version for noisy wafer stages

## Quality and supply
Silicone ESD-Protected Cleanroom Control Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/besilen-silicone-esd-protected-cleanroom-control-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Dielectric spark / high-voltage withstand test — 100 % in-line spark and AC/DC dielectric withstand per DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone | Every manufactured length
Routine test | Conductor DC resistance & continuity check — Within maximum 20 °C resistance limit specified for Silicone ESD Cleanroom Control Cable | Every spool or drum length
Sample test | Insulation resistance & dimensional verification — Wall thickness, concentricity and insulation resistance per DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone | Per production batch
Type test | Environmental, mechanical & EMC qualification — Qualified to DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone thermal, mechanical and environmental performance criteria | Type qualification
Standard / approval | DIN EN 61340-5-1 ESD / ISO 14644-1 Class 1 Cleanroom / EN 50525-2-83 Silicone
Standard / approval | CE (2014/35/EU) & RoHS 3 (2015/863/EU) Compliant
Standard / approval | REACH SVHC Compliance Verified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX Silicone ESD CONTROL 7G0.75 300/500V -40/+180C EN 61340-5-1
Supply | Delivery form: Export wooden drums, tactical reels or coils
Supply | Standard lengths: 100 m · 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP