## Request a quote
Request a quotation for Submersible Pump Cable
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/flat-submersible-pump-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Submersible Pump Cable – Dimensions & masses (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/flat-submersible-pump-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0282 / BS 6920 / KTW / ACS / NSF-61. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores × Size mm² | Flat H × W mm | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| Flat 3×1.5 | 3 × 1.5 mm² | 5.2 × 11.8 mm | 5.2 | 43.2 | 105 | 20.8 | Submersible Pump Cable size schedule
| Flat 3×2.5 | 3 × 2.5 mm² | 5.8 × 13.5 mm | 5.8 | 72 | 145 | 23.2 | Submersible Pump Cable size schedule
| Flat 3×4.0 | 3 × 4.0 mm² | 6.8 × 16.2 mm | 6.8 | 115.2 | 210 | 27.2 | Submersible Pump Cable size schedule
| Flat 3×6.0 | 3 × 6.0 mm² | 7.5 × 18.0 mm | 7.5 | 172.8 | 280 | 30 | Submersible Pump Cable size schedule
| Flat 3×10 | 3 × 10 mm² | 9.2 × 22.4 mm | 9.2 | 288 | 445 | 36.8 | Submersible Pump Cable size schedule
| Flat 3×16 | 3 × 16 mm² | 10.6 × 26.0 mm | 10.6 | 460.8 | 660 | 42.4 | Submersible Pump Cable size schedule
| Flat 3×25 | 3 × 25 mm² | 12.5 × 31.2 mm | 12.5 | 720 | 995 | 50 | Submersible Pump Cable size schedule
| Flat 3×35 | 3 × 35 mm² | 13.8 × 35.0 mm | 13.8 | 1008 | 1340 | 55.2 | Submersible Pump Cable size schedule
| Flat 4G1.5 | 4G 1.5 mm² | 5.4 × 15.2 mm | 5.4 | 57.6 | 135 | 21.6 | Submersible Pump Cable size schedule
| Flat 4G2.5 | 4G 2.5 mm² | 6.2 × 17.8 mm | 6.2 | 96 | 195 | 24.8 | Submersible Pump Cable size schedule
| Flat 4G4.0 | 4G 4.0 mm² | 7.2 × 21.0 mm | 7.2 | 153.6 | 280 | 28.8 | Submersible Pump Cable size schedule
| Flat 4G6.0 | 4G 6.0 mm² | 8.0 × 23.8 mm | 8 | 230.4 | 380 | 32 | Submersible Pump Cable size schedule
| Flat 4G10 | 4G 10 mm² | 9.6 × 29.2 mm | 9.6 | 384 | 595 | 38.4 | Submersible Pump Cable size schedule
| Flat 4G16 | 4G 16 mm² | 11.0 × 34.0 mm | 11 | 614.4 | 880 | 44 | Submersible Pump Cable size schedule
| Flat 4G25 | 4G 25 mm² | 13.0 × 41.0 mm | 13 | 960 | 1320 | 52 | Submersible Pump Cable size schedule
| Flat 4G35 | 4G 35 mm² | 14.5 × 46.0 mm | 14.5 | 1344 | 1780 | 58 | Submersible Pump Cable size schedule
Dimensions and tolerances conform to DIN VDE 0282 / BS 6920 / KTW / ACS / NSF-61.

## Electrical data
Submersible Pump Cable – Electrical data (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/flat-submersible-pump-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0282 / BS 6920 / KTW / ACS / NSF-61. Values for your order are confirmed in the quotation.
Cores × Size mm² | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
3 × 1.5 mm² | 13.3 | 23 | 18
3 × 2.5 mm² | 7.98 | 31 | 25
3 × 4.0 mm² | 4.95 | 42 | 34
3 × 6.0 mm² | 3.3 | 54 | 43
3 × 10 mm² | 1.91 | 75 | 60
3 × 16 mm² | 1.21 | 100 | 80
3 × 25 mm² | 0.78 | 133 | 106
3 × 35 mm² | 0.554 | 164 | 131
4G 1.5 mm² | 13.3 | 23 | 18
4G 2.5 mm² | 7.98 | 31 | 25
4G 4.0 mm² | 4.95 | 42 | 34
4G 6.0 mm² | 3.3 | 54 | 43
4G 10 mm² | 1.91 | 75 | 60
4G 16 mm² | 1.21 | 100 | 80
4G 25 mm² | 0.78 | 133 | 106
4G 35 mm² | 0.554 | 164 | 131
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
Submersible Pump Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/flat-submersible-pump-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0282 / BS 6920 / KTW / ACS / NSF-61. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 450/750 V & 0.6/ (Up to 1.2 kV max. AC)
Key data | Immersion depth | AD8 · up to 500 (50 bar hydrostatic pressure)
Key data | Potable approvals | KTW / WRAS / ACS (Plus NSF/ANSI 61 drinking water)
Key data | Profile | Flat parallel (3 (Fits narrow borehole clearance)
Key data | Cross-sections | 1.5 to 120 mm² (3-core & 4-core (with PE))
Key data | Water temp | Up to +70 / +85 (+90 °C max conductor temp)
Electrical | Rated voltage (U0/U) | 450/750 V & 0.6/1 kV AC (up to 1.2 kV AC max.)
Electrical | AC test voltage (water bath) | 3.5 kV rms for 5 minutes
Electrical | Insulation resistance in water | ≥1,000 MΩ·km at +20 °C
Thermal | Max. conductor operating temperature | +90 °C continuous · +250 °C short-circuit
Thermal | Permissible water temperature | Up to +70 °C (KTW/WRAS potable) · up to +85 °C (industrial water)
Mechanical | Hydrostatic immersion rating | AD8 permanent submersion up to 500 m depth (50 bar / 5.0 MPa)
Mechanical | Minimum bending radius | 4 × cable flat thickness (H) for fixed riser clamping
Resistance | Drinking-water hygiene & leaching | Zero organic carbon (TOC), taste, odour or heavy-metal migration per BS 6920 & KTW-BWGL
Resistance | Water uptake & hydrolysis | <1.5 mg/cm² gravimetric water absorption; immune to chlorinated water
Standards | Potable-water certifications | UBA KTW-BWGL / DVGW W270 (Germany), WRAS BS 6920 (UK), ACS (France), NSF/ANSI 61 (USA)
Standards | Electrical reference standards | DIN VDE 0282 / HD 22 / IEC 60228 Class 5
Identification | Core identification | 3-core: Brown, Black, Grey (or Blue, Brown, Black) · 4G: + Green/Yellow
Identification | Outer jacket colour | Drinking-water Blue (RAL 5015) or Black

## Construction
Submersible Pump Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/flat-submersible-pump-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0282 / BS 6920 / KTW / ACS / NSF-61. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 flexible copper (IEC 60228) | Fine-stranded bare (or tinned) annealed copper conductors arranged in a parallel flat plane | IEC 60228
2 | High-grade EPR / HEPR rubber (3GI3) | Cross-linked ethylene-propylene rubber insulation with ultra-low water absorption and high insulation resistance | VDE 0282
3 | Potable-water EPDM flat sheath | Peroxide-cured, taste- and odour-free EPDM compound certified to KTW-BWGL, WRAS BS 6920, ACS and NSF-61 (Blue or Black) | BS 6920
| Flat 3-Core (3 × 1.5 to 3 × 95 mm² — Brown, Black, Grey or Blue/Brown/Black) | 3-core flat borehole drop cable or motor tail for 3-phase submersible motors with separate earth or earthed riser pipe.
| Flat 4-Core / 4G (4G1.5 to 4G120 mm² — Brown, Black, Grey + Green/Yellow) | 4-core flat borehole cable integrating a full-size green/yellow protective earth conductor inside the same flat web.

## Quality and supply
Submersible Pump Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/flat-submersible-pump-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0282 / BS 6920 / KTW / ACS / NSF-61. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC 5-minute water-bath test & DC resistance — Zero breakdown; resistance per IEC 60228 Class 5 | 100 % of drums
Sample test | Gravimetric water absorption & hot-set curing check — Water absorption <1.5 mg/cm²; hot-set elongation ≤175 % | Every batch
Type test | BS 6920 / KTW / ACS organoleptic, TOC & microbial tests — Certified safe for human drinking-water contact | Type qualification
Standard / approval | KTW-BWGL & DVGW W270 (Germany)
Standard / approval | WRAS BS 6920 (UK)
Standard / approval | ACS Attestation de Conformité Sanitaire (France)
Standard / approval | NSF/ANSI 61 Drinking Water
Standard / approval | CE / RoHS 3
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX FLAT SUBMERSIBLE PUMP CABLE 0.6/1kV [N×mm2] EPDM KTW WRAS ACS AD8 500M [lot/m]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP