## Request a quote
Request a quotation for Subsea Caisson Cable
Share governing standard (IEC/IEEE 1580/NEK 606/BS 6883), voltage rating, core count × cross-section, armour/sheath type and total length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/subsea-caisson-armoured-power-data-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
0.6/1 kV Subsea Caisson Pump Power & Screened Sensor Data Steel-Braid – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/subsea-caisson-armoured-power-data-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Breaking / tensile kN ≈ | Min. bend R mm | Series
| Subsea Caisson Cable 3×16+1G16 mm² | 3 × 16 + 1G16 mm² (or 1C×50 mm²) | IEC 60228 Class 2/5 Cu/SnCu | 22.4 | 920 | 18.5 | 135 | Subsea Caisson Cable Construction Schedule (−30…+90 °C)
| Subsea Caisson Cable 3×35+1G16 mm² | 3 × 35 + 1G16 mm² (or 1C×150 mm²) | IEC 60228 Class 2/5 Cu/SnCu | 28.8 | 1690 | 32 | 175 | Subsea Caisson Cable Construction Schedule (−30…+90 °C)
| Subsea Caisson Cable 3×95+1G50 mm² | 3 × 95 + 1G50 mm² (or 1C×300 mm²) | IEC 60228 Class 2/5 Cu/SnCu | 41.2 | 3680 | 58 | 250 | Subsea Caisson Cable Construction Schedule (−30…+90 °C)
Custom core cross-sections, pair/fibre counts, armour breaking loads and continuous winch/seabed lengths available per 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification.

## Electrical, optical & thermal p
0.6/1 kV Subsea Caisson Pump Power & Screened Sensor Data Steel-Braid – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/subsea-caisson-armoured-power-data-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 16 + 1G16 mm² (or 1C×50 mm²) | 1.15 | 0.6/1 kV (98 A) | −30…+90 °C
3 × 35 + 1G16 mm² (or 1C×150 mm²) | 0.524 | 0.6/1 kV (158 A) | −30…+90 °C
3 × 95 + 1G50 mm² (or 1C×300 mm²) | 0.193 | 0.6/1 kV (285 A) | −30…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
0.6/1 kV Subsea Caisson Pump Power & Screened Sensor Data Steel-Braid – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/subsea-caisson-armoured-power-data-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV (Tested per Subsea Caisson Pump / 0.6/1 k)
Key data | Operating temp. | −30…+90 °C (Continuous subsea & offshore service)
Key data | Min. bend radius | 8 × OD (Winch sheave, chute & seabed routing)
Key data | Core / conductor | Caisson Pump Pow (Stranded tinned copper conductors with w)
Key data | Outer protection | Flame-Retardant (High-strength flame-retardant polyuretha)
Key data | Standard | Subsea Caisson P (0.6/1 kV Subsea Caisson Pump Power + Scr)
Electrical | Rated voltage / transmission duty | 0.6/1 kV (0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification)
Electrical | Core / conductor construction | Caisson Pump Power Conductors (4 Cores) — Stranded tinned copper conductors with water-resistant XLPO insulation
Electrical | Primary dielectric / buffering | Shielded Sensor Data Twisted Pairs (4×2) — Individually foil-screened pairs for caisson level, vibration & temp monitoring
Thermal | Continuous operating temperature | −30…+90 °C (subsea & offshore duty)
Thermal | Hydrostatic & thermal stability | Verified thermal and hydrostatic stability per 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel winch reel
Mechanical | Outer protection / armouring | Flame-Retardant Heavy PUR Outer Jacket — High-strength flame-retardant polyurethane outer sheath
Mechanical | Minimum bending radius | 8 × OD
Mechanical | Armour, strength member & mechanical duty | PUR Inner Sheath & Galvanized Steel Braid — Waterproof PUR inner jacket + galvanized steel wire braid armour
Resistance | Seawater, hydrostatic & hydrolysis resistance | Engineered for continuous seawater immersion, pressure cycling and hydrolysis resistance per 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification
Resistance | Oil, drilling mud & abrasion resistance | Resistant to marine hydraulic oils, salt mist, winch sheave wear and seabed abrasion per 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification
Standards | Environmental & test standards | IEC 60228 / IEC 60794 / ITU-T G.972 / IEEE 1580 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | Subsea Caisson Cable
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Flame-Retardant )
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
0.6/1 kV Subsea Caisson Pump Power & Screened Sensor Data Steel-Braid – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/subsea-caisson-armoured-power-data-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Caisson Pump Power Conductors (4 Cores) | Stranded tinned copper conductors with water-resistant XLPO insulation
2 | Shielded Sensor Data Twisted Pairs (4×2) | Individually foil-screened pairs for caisson level, vibration & temp monitoring
3 | PUR Inner Sheath & Galvanized Steel Brai | Waterproof PUR inner jacket + galvanized steel wire braid armour
4 | Flame-Retardant Heavy PUR Outer Jacket | High-strength flame-retardant polyurethane outer sheath
| Subsea Caisson Cable — Standard Subsea & Offshore Execution | Built to 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification with caisson pump power conductors (4 cores) and flame-retardant heavy pur outer jacket
| Subsea Caisson Cable — Custom Continuous Winch / Reel Length | Available in custom continuous subsea winch, tow or seabed lengths with water-blocked terminations
| Subsea Caisson Cable — Hydrostatic, Tensile & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, optical OTDR / DC resistance & tensile test report

## Quality and supply
0.6/1 kV Subsea Caisson Pump Power & Screened Sensor Data Steel-Braid – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/subsea-caisson-armoured-power-data-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, optical OTDR continuity & dimensional verification (0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification) — DC resistance at 20 °C / optical attenuation and outer diameter within 0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification) — Zero dielectric breakdown and verified insulation resistance for 0.6/1 kV rating | Every manufactured drum length
Type test | Hydrostatic pressure, tensile breaking load & water-blocking qualification (0.6/1 kV Subsea Caisson Pump Power + Screened Data Pairs Steel-Braid Armoured PUR Specification) — Verified subsea pressure integrity, torque-balanced tensile performance and thermal stability across −30…+90 °C | Type qualification & periodic lot audit
Standard / approval | Subsea Caisson Pump / 0.6/1 kV Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX Subsea Caisson Cable Subsea Caisson Pump / 0.6/1 kV 0.6/1 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel oceanographic winch reels or submarine turntables
Supply | Standard lengths: 500 m, 1,000 m, 3,000 m, 6,000 m or custom continuous subsea lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom subsea builds)
Supply | Lead time: 2–6 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP