## Request a quote
Request a quotation for Super-Trex 600 V Welding Cable
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/600-v-heavy-duty-flexible-welding-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Super-Trex 600 V Welding Cable – 34 AWG strand count, dimensions & ampacity (7)
TEBAOFLEX ¦ https://tebaoflex.com/cables/600-v-heavy-duty-flexible-welding-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL Listed 600 V Welding / CSA C22.2 No. 96 / NEC Art. 630. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order size | 34 AWG Tinned Cu strands | Nominal Ø mm | Weight ≈ kg/km | 600V Cont. A | Weld 60% A | Series
| 600V Class M 2 AWG | 1,666 × 34 AWG (33.6 mm²) | 12.7 | 430 | 190 | 300 | AWG Sizes (6 AWG to 4/0 AWG)
| 600V Class M 1 AWG | 2,107 × 34 AWG (42.4 mm²) | 14.5 | 550 | 220 | 350 | AWG Sizes (6 AWG to 4/0 AWG)
| 600V Class M 1/0 AWG | 2,646 × 34 AWG (53.5 mm²) | 16 | 685 | 260 | 420 | AWG Sizes (6 AWG to 4/0 AWG)
| 600V Class M 2/0 AWG | 3,325 × 34 AWG (67.4 mm²) | 17.5 | 845 | 300 | 500 | AWG Sizes (6 AWG to 4/0 AWG)
| 600V Class M 4/0 AWG | 5,320 × 34 AWG (107 mm²) | 21.1 | 1310 | 405 | 650 | AWG Sizes (6 AWG to 4/0 AWG)
| 600V Class M 350 MCM | 8,806 × 34 AWG (177 mm²) | 26.7 | 2140 | 515 | 850 | kcmil / MCM Sizes (250 to 500 MCM)
| 600V Class M 500 MCM | 12,540 × 34 AWG (253 mm²) | 30.7 | 2990 | 620 | 1050 | kcmil / MCM Sizes (250 to 500 MCM)
6 AWG (665×34 AWG, 9.7 mm OD) and 4 AWG (1,064×34 AWG, 11.2 mm OD) are also stocked for lighter TIG/MIG torches and ground straps.

## Technical data
Super-Trex 600 V Welding Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/600-v-heavy-duty-flexible-welding-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL Listed 600 V Welding / CSA C22.2 No. 96 / NEC Art. 630. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 600 V AC / DC (Dual-rated Welding & Power)
Key data | Size range | 6 AWG to 500 MCM (13.3 mm² to 253 mm²)
Key data | Stranding class | Class M (34 AWG) (0.16 mm rope-lay Tinned Cu)
Key data | Jacket compound | Heavy-Duty TSE (+105 °C · Oil, slag & UV proof)
Key data | Cold flexibility | -50 °C to +105 ° (All-weather outdoor service)
Key data | Flame & safety | UL VW-1 / CSA FT (MSHA flame-resistant option)
Electrical | Rated voltage | 600 V AC / DC (UL Listed Welding & Power Lead)
Electrical | Factory dielectric test | 3,000 V AC rms & 10 kV spark test on 100 % of reel length
Electrical | Max. DC resistance @ 20 °C | 0.528 Ω/km (2 AWG) · 0.210 Ω/km (2/0 AWG) · 0.132 Ω/km (4/0 AWG)
Electrical | 600 V NEC ampacity (air) | 190 A (2 AWG) · 300 A (2/0 AWG) · 405 A (4/0 AWG) · 515 A (350 MCM)
Thermal | Continuous conductor temp. | +105 °C Dry / +90 °C Wet or Oil
Thermal | Cold-bend flexibility | -50 °C cold bend without cracking
Thermal | Short-circuit / slag contact | +250 °C short-circuit · Chars without melting under hot weld slag
Mechanical | Individual strand gauge | 34 AWG (0.160 mm / 0.0063 in) per ASTM B172 Class M
Mechanical | 600 V TSE wall thickness | 2.03 mm (6–1 AWG) · 2.41 mm (1/0–4/0 AWG) · 2.79 mm (250–500 MCM)
Mechanical | Min. bend radius | 4 × OD (static) · 5 × OD (dynamic flexing)
Resistance | Oil, coolant & acid | Passes UL Oil Res I & II (+60/+75 °C oil immersion) & cutting fluid tests
Resistance | Flame retardancy | UL VW-1 · CSA FT1 · MSHA flame-resistant print available
Resistance | UV, ozone & water | Sunlight resistant (720 h UV) and ozone chamber qualified
Standards | North American approvals | UL 600 V Welding Cable · CSA C22.2 No. 96 · NEC Article 630
Standards | Conductor standard | ASTM B33 (Tinned Cu) & ASTM B172 Class M (34 AWG)
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Surface print legend | SUPER-TREX 600V WELDING & POWER CABLE 34 AWG CLASS M TINNED CU 105C (UL) CSA
Identification | Customs tariff (HS) | 8544.4993
Identification | Footage markings | Sequential 1-foot markings printed along entire reel

## Construction
Super-Trex 600 V Welding Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/600-v-heavy-duty-flexible-welding-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL Listed 600 V Welding / CSA C22.2 No. 96 / NEC Art. 630. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class M (34 AWG / 0.16 mm) rope-lay tinned copper conductor | Extra-fine 34 AWG (0.16 mm) tin-coated annealed copper wires bunched into multi-rope lay per ASTM B33 & ASTM B172 Class M
2 | Low-friction polyester separator tape | Helically wrapped Mylar/PET separator tape over the rope-lay tinned copper
3 | 600 V Heavy-Duty Thermoset Elastomer (TSE) jacket | Thick-wall cross-linked thermoset elastomer (CPE / PCP / EPDM blend) rated 600 V, -50 °C to +105 °C in Yellow, Orange, Black or Red
| Super-Trex 600 V Yellow / Orange (6 AWG to 500 MCM) | High-visibility Safety Yellow or Orange 600 V Class M tinned copper welding & portable power lead
| Super-Trex 600 V Black / Red (6 AWG to 500 MCM) | Polarity-coded Black and Red 600 V Class M tinned copper leads for DC welding stingers, load banks and battery systems

## Quality and supply
Super-Trex 600 V Welding Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/600-v-heavy-duty-flexible-welding-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL Listed 600 V Welding / CSA C22.2 No. 96 / NEC Art. 630. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 3,000 V AC water-tank dielectric, 10 kV spark & DC resistance test — Zero breakdown and Class M tinned copper DC R within ASTM B172 limits | Every manufactured reel
Type test | -50 °C cold mandrel bend, Oil Res I/II & VW-1/FT1 flame test — Zero jacket cracking at -50 °C and ≥ 75 % tensile retention after hot oil | UL / CSA listing test
Sample test | 34 AWG tin coating continuity (ASTM B33 polysulfide test) — Uniform tin plating free of bare copper spots on all 34 AWG wires | Per conductor lot
Standard / approval | UL Listed 600 V Welding & Power
Standard / approval | CSA C22.2 No. 96 FT1
Standard / approval | NEC Article 630 & ASTM B172
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX SUPER-TREX 600V WELDING & POWER 2/0 AWG 34 AWG CLASS M TINNED CU 105C (UL) CSA FT1
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP