## Request a quote
Request a quotation for Symmetrical-Ground 1kV WTTC / 2kV VFD
Share drive kW/voltage (0.6/1 kV, 1,000 V WTTC or 2,000 V RHW-2), 3+3 symmetrical or 4G cross-section, shield type (dual Cu tape or foil+braid) and total length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/symmetrical-ground-1kv-wttc-2kv-cu-tape-vfd-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
Symmetrical-Ground 1,000 V UL WTTC / 2,000 V UL RHW-2 (3 Phase + 3 Spl – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/symmetrical-ground-1kv-wttc-2kv-cu-tape-vfd-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Max. pulling kN ≈ | Min. bend R mm | Series
| Symmetrical-Ground 1kV WTTC 4G16 / 3×16+3G2.5 | 4G16 mm² (or 3×6 AWG + 3G10 AWG) | IEC 60228 Class 5 / Class K Cu | 21.8 | 790 | 9.5 | 130 | Symmetrical-Ground 1kV WTTC / 2kV VFD Construction Schedule (−40…+90 °C)
| Symmetrical-Ground 1kV WTTC 4G50 / 3×50+3G10 | 4G50 mm² (or 3×1 AWG + 3G6 AWG) | IEC 60228 Class 5 / Class K Cu | 31.4 | 2140 | 22.5 | 190 | Symmetrical-Ground 1kV WTTC / 2kV VFD Construction Schedule (−40…+90 °C)
| Symmetrical-Ground 1kV WTTC 3×150+3G25 VFD | 3×150 + 3G25 mm² (or 3×350 kcmil) | IEC 60228 Class 5 / Class K Cu | 47.2 | 5480 | 58 | 285 | Symmetrical-Ground 1kV WTTC / 2kV VFD Construction Schedule (−40…+90 °C)
Custom conductor cross-sections, core counts, pre-lugged tower kits and drum lengths available per UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification.

## Electrical & thermal parameters
Symmetrical-Ground 1,000 V UL WTTC / 2,000 V UL RHW-2 (3 Phase + 3 Spl – Electrical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/symmetrical-ground-1kv-wttc-2kv-cu-tape-vfd-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ Ω/km | Rating / Impedance | Operating temp.
4G16 mm² (or 3×6 AWG + 3G10 AWG) | 1.15 | 1,000 V WTTC / 2,000 V RHW-2 (98 A VFD) | −40…+90 °C
4G50 mm² (or 3×1 AWG + 3G6 AWG) | 0.387 | 1,000 V WTTC / 2,000 V RHW-2 (195 A VFD) | −40…+90 °C
3×150 + 3G25 mm² (or 3×350 kcmil) | 0.129 | 1,000 V WTTC / 2,000 V RHW-2 (395 A VFD) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, AC high-voltage spark/dielectric and dimensional verification.

## Technical data
Symmetrical-Ground 1,000 V UL WTTC / 2,000 V UL RHW-2 (3 Phase + 3 Spl – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/symmetrical-ground-1kv-wttc-2kv-cu-tape-vfd-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1,000 V WTTC / 2 (Tested per UL 2277 WTTC / UL 44 RHW-2)
Key data | Operating temp. | −40…+90 °C (Cold-climate & nacelle wind service)
Key data | Min. bend radius | 8 × OD (Drip-loop, hub & tower routing)
Key data | Core / conductor | XHHW-2 / RHW-2 P (Flexible stranded copper phase cores (14)
Key data | Outer protection | Cold & Sunlight- (UL WTTC 1,000 V & RHW-2 2,000 V wind con)
Key data | Standard | UL 2277 WTTC / U (UL Subject 2277 WTTC 1,000 V & UL 44 RHW)
Electrical | Rated voltage / operating system | 1,000 V WTTC / 2,000 V RHW-2 (UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification)
Electrical | Core / conductor construction | XHHW-2 / RHW-2 Phase Conductors (3 Cores) — Flexible stranded copper phase cores (14 AWG to 500 kcmil)
Electrical | Primary dielectric / insulation | Symmetrical Tri-Sectional Grounds (3 Cores) — Three balanced interstitial ground cores canceling common-mode voltage
Thermal | Continuous operating temperature | −40…+90 °C (wind turbine nacelle, hub & tower duty)
Thermal | Low-temperature torsion & cold bend | Verified cold-flex and torsion endurance across −40…+90 °C per UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel cable drum
Mechanical | Outer jacket / sheath protection | Cold & Sunlight-Resistant Heavy Polymer Jacket — UL WTTC 1,000 V & RHW-2 2,000 V wind converter drive sheath
Mechanical | Minimum bending radius | 8 × OD
Mechanical | Intermediate screen / separator / core layer | Dual Helical Copper Tape EMC Shield (100%) — Two overlapping copper tapes providing low-impedance EMI return path
Resistance | Oil, grease, ozone & UV resistance | Resistant to wind turbine gearbox oil, hydraulic fluid, ozone and UV weathering per UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification
Resistance | Flame retardancy & smoke/halogen emission | Flame-retardant and environmental performance verified per UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification
Standards | Conductor & flame/test standards | IEC 60228 / IEC 60332-1-2 & -3 / UL 2277 WTTC / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | Symmetrical-Ground 1kV WTTC / 2kV VFD
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Cold & Sunlight-)
Identification | Customs tariff (HS) | 8544.49 / 8544.60

## Construction
Symmetrical-Ground 1,000 V UL WTTC / 2,000 V UL RHW-2 (3 Phase + 3 Spl – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/symmetrical-ground-1kv-wttc-2kv-cu-tape-vfd-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | XHHW-2 / RHW-2 Phase Conductors (3 Cores | Flexible stranded copper phase cores (14 AWG to 500 kcmil)
2 | Symmetrical Tri-Sectional Grounds (3 Cor | Three balanced interstitial ground cores canceling common-mode voltage
3 | Dual Helical Copper Tape EMC Shield (100 | Two overlapping copper tapes providing low-impedance EMI return path
4 | Cold & Sunlight-Resistant Heavy Polymer | UL WTTC 1,000 V & RHW-2 2,000 V wind converter drive sheath
| Symmetrical-Ground 1kV WTTC / 2kV VFD — Standard Wind Turbine Execution | Built to UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification with xhhw-2 / rhw-2 phase conductors (3 cores) and cold & sunlight-resistant heavy polymer jacket
| Symmetrical-Ground 1kV WTTC / 2kV VFD — Pre-Cut Tower / Drip-Loop Kit | Available on bulk export reels or pre-cut to turbine tower section and nacelle drip-loop lengths
| Symmetrical-Ground 1kV WTTC / 2kV VFD — Cold Torsion & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, conductor DC resistance & cold-torsion qualification report

## Quality and supply
Symmetrical-Ground 1,000 V UL WTTC / 2,000 V UL RHW-2 (3 Phase + 3 Spl – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/symmetrical-ground-1kv-wttc-2kv-cu-tape-vfd-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification) — DC resistance at 20 °C and insulation/sheath wall thickness within UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification limits | Every manufactured drum length
Routine test | AC high-voltage dielectric & insulation resistance test (UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification) — Zero dielectric breakdown and verified insulation resistance for 1,000 V WTTC / 2,000 V RHW-2 rating | Every manufactured drum length
Type test | Low-temperature drip-loop torsion, oil & flame qualification (UL Subject 2277 WTTC 1,000 V & UL 44 RHW-2 2,000 V Symmetrical 3+3 Dual Cu-Tape VFD Specification) — Verified cold torsion cycle endurance, oil resistance and flame retardancy across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | UL 2277 WTTC / UL 44 RHW-2 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX Symmetrical-Ground 1kV WTTC / 2kV VFD UL 2277 WTTC / UL 44 RHW-2 1,000 V WTTC / 2,000 V RHW-2 CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel reels or pre-cut wind turbine tower & drip-loop kits
Supply | Standard lengths: 500 m, 1,000 m or custom cut-to-length nacelle drip-loop and tower section sets
Supply | MOQ: 100 m (standard configurations) · 300 m (custom wind builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP